## Main
[5 empty] | Brief version | Scheduled
Assessment Software | [5 empty] | Completed
Version | CASBEE-BD_NCe_2014(v.2.1) |  |  |  | Zone 1 | 地域区分Ⅰ | 1
n Assessment Manual : | CASBEE for Building (New Construction) 2014 Edition |  |  |  | Zone 2 | 地域区分Ⅱ | 2
[5 empty] | Zone 3 | 地域区分Ⅲ | 3
1) Summary input |  |  |  |  | Zone 4 | 地域区分Ⅳ | 4
[1] Building outline |  |  |  |  | Zone 5 | 地域区分Ⅴ | 5
[5 empty] | Zone 6 | 地域区分Ⅵ | 6
n Building Name | XXX Building |  |  |  | Zone 7 |  | 7
n Location / Climate zone | XX City, XX Prefecture |  |  |  | Zone 8 |  | 8
９地域
n Area / Zone | Commercial area, Fire protection zone
n Date of completion | 2016-12-01 | (Scheduled/Completed) |  | Scheduled |  |  | #N/A
n Site Area | XXX | m2
n Construction Area | XXX | m2
n Gross Floor Area | 0 | m2
n Building Type | ○○
n Number of Floors | + XX F
n Structure | S |  |  |  | S | RC | SRC | Wood
n Occupancy | XX | Occupants (assumed) |  |  | 1
n Average Annual Occupancy | XXX | hrs./yr. (assumed)
[2] Implementation of Assessment |  |  |  |  | EB |  |  | NC | CASBEE-EB for school
n Assessment date | 2014-07-08 |  |  |  | Preliminary design stage | 1 |  | Preliminary design stage | Brief assessment
n Assessor | XXXXX |  |  |  | Execution design stage | 2 |  | Execution design stage | Assessed by Energy Saving plan
n Date of confirmation | 2014-07-10 |  |  |  | Construction completion stage | 2 |  | Construction completion stage
n Confirmed by | XXXXX |  |  |  | 2
n LCCO2 calculation | Standard calculation | --> Input LCCO2 Calculation Conditions Sheet (standard calculation) |  |  | Standard calculation |  |  | --> Input LCCO2 Calculation Conditions Sheet (standard calculation)
[5 empty] | Individual calculation |  |  | --> Input LCCO2 Calculation Conditions Sheet (Individual calculation)
2) Entry for individual building type
[1] Floor area of each building type | [5 empty] | common | ratio | Residential
Offices | 0 | m2 Office |  | m2 | Offices | 0 | #DIV/0! |  |  | 0 | 事務所 | 事務所 | 0
|  | Government buildings |  | m2 | [5 empty] | 0 |  | 官公庁 | 0
Schools | 0 | m2 Kindergartens/ nursery schools |  | m2 | Schools | 0 | #DIV/0! |  |  | 0 | 学校等 | 幼稚園・保育園 | 0
|  | Elementary/junior high schools (Hokkaido) |  | m2 | [5 empty] | 0 |  | 小中（北海道） | 0
|  | Elementary/junior high schools (other than Hokkaido) |  | m2 | [5 empty] | 0 |  | 小中（その他） | 0
|  | High schools |  | m2 | [5 empty] | 0 |  | 高校 | 0
|  | Universities/technical colleges |  | m2 | [5 empty] | 0 |  | 大学・専門学校 | 0
Retailers | 0 | m2 Department stores, supermarkets |  | m2 | Retailers | 0 | #DIV/0! |  |  | 0 | 物販店舗等 | デパート・スーパー | 0
|  | Other stores |  | m2 | [5 empty] | 0 |  | その他物販 | 0
Restaurants |  | m2 |  |  | Restaurants | 0 | #DIV/0! |  |  | 0 | 飲食店 |  | 0
Halls | 0 | m2 Theatres/halls |  | m2 | Halls | 0 | #DIV/0! |  |  | 0 | 集会所等 | 劇場・ホール | 0
|  | Exhibition facilities |  | m2 | [5 empty] | 0 |  | 展示施設 | 0
|  | Sports facilities |  | m2 | [5 empty] | 0 |  | スポーツ施設 | 0
Factories |  | m2 energy saving plan |  | m2 | Factories | 0 | #DIV/0! |  |  | 0 | 工場 |  | 0
Hospitals |  | m2 |  |  | Hospitals | 0 | #DIV/0! | 0 |  | 0 | 病院 |  | 0
Hotels |  | m2 |  |  | Hotels | 0 | #DIV/0! | 0 |  | 0 | ホテル・旅館 |  | 0
Non-residential Subtotal | 0 | m2 |  |  | Non-residential Subtotal |  |  |  |  | 0
Apartments | 0 | m2 Private area |  | m2 | Apartments | 0 | #DIV/0! | 0 |  | 0 | 集合住宅 | 専有部 | 0
|  | Common area |  | m2 | [7 empty] | 共用部 | 0
[5 empty] | Total | 0 | #DIV/0! | 0
[2] Ratio of Residential & Accommodation Section
n Proportion of gross floor area designated as in-patient rooms
n Proportion of gross floor area designated as guest rooms
n Proportion of gross floor area designate as dwelling units |  |  |  | 0
3) Results Output
Score Sheet | lScore
Assessment Result Sheet | lResult |  | lLCCO2 calculation
LCCO2 Calculation Conditions Sheet | lStandard calculation |  | lIndividual calculation
Building type | Types included
Offices | Offices, government buildings, libraries, museums, post offices, etc.
Schools | Elementary schools, junior high schools, high schools, universities, technical colleges, higher vocational school and other school types
Retailers | Department stores, supermarkets, etc.
Restaurants | Restaurants, canteens, cafes, etc.
Halls | Auditoriums, halls, bowling lanes, gymnasiums, theaters, movie theaters, pachinko parlors exhibition facilities, etc.
Factories | Factories, garages, warehouses, spectator stands, wholesale markets, computer rooms, etc.
Hospitals | Hospitals, homes for elderly, welfare homes for the handicapped, etc.
Hotels | Hotels, inn, etc.
Apartments | Apartments (detached houses are not applied)
Note on B41: Fill in if the assessment is confirmed by third party.
Note on F68: Input the ratio, in the range 0-1.0
Note on F69: Input the ratio, in the range 0-1.0

## Result
←
[7 empty] | n Manual: |  | CASBEE for Building (New Construction) 2014 Edition |  | n Software: | CASBEE-BD_NCe_2014(v.2.1)
1-1 Building Outline | [9 empty] | 1-2 Appearance |  |  |  |  | BEE rank |  |  | radar chart
Building Name |  | XXX Building |  |  |  | Number of Floors |  | + XX F | [6 empty] | SQ | #DIV/0! |  |  | radar chart | background | 4 | 2 | Score(Round Down) | std
Location |  | XX City, XX Prefecture |  |  |  | Structure |  | S | [6 empty] | SLR | #VALUE! |  | Q2 | Q2 Quality of Service | 5 | 4 | 2 | #DIV/0! | 3
Area / Zone |  | Commercial area, Fire protection zone |  |  |  | Occupancy |  | XX | people | [5 empty] | Q | #DIV/0! |  | Q3 | Q3 Outdoor Environment on Site | 5 | 4 | 2 | #DIV/0! | 3
Climate Zone | [5 empty] | Annual Occupancy |  | XXX | hrs. /yr. | [5 empty] | L | #VALUE! |  | LR3 | LR3 Off-site Environment | 5 | 4 | 2 | #DIV/0! | 3
Building Type | [5 empty] | Assessment phase |  |  |  |  | Appearance, etc. |  |  |  | BEE | #DIV/0! |  | LR2 | LR2 Resources & Materials | 5 | 4 | 2 | #DIV/0! | 3
Completion |  | 2016-12-01 |  | Scheduled |  | Assessment date |  | 2014-07-08 |  |  | When you paste a figure, |  |  |  | BEE(Round) | #DIV/0! |  | LR1 | LR1 Energy | 5 | 4 | 2 | #VALUE! | 3
Site Area |  |  | XXX | m2 |  | Assessor |  | XXXXX |  |  | unlock the sheet's protection. | [6 empty] | Q1 | Q1 Indoor Environment | 5 | 4 | 2 | #DIV/0! | 3
Construction Area |  |  | XXX | m2 |  | Date of approval |  | 2014-07-10 | [6 empty] | Rank(red star) | #DIV/0!
Gross Floor Area |  |  | 0 | m2 |  | Approved by |  | XXXXX | [6 empty] | (blank star) | #DIV/0!
改修工事期間 | [9 empty] | 改修対象項目 | 躯体
改修目的 | [10 empty] | 外装
改修後の想定使用年数 | [10 empty] | 内装
現在までの主な改修履歴 | [10 empty] | 設備
2-1 Building Environmental Efficiency (rank & chart) | [5 empty] | 2-2 Assessment results of Major categories (radar chart) |  |  |  | 2-3 Lifecycle CO2 (Global warming impact chart） |  |  |  |  | BEEグラフ | Standard | Subject | origin
[15 empty] | BEEの分母側(L) |  | #VALUE! | 0 |  | X目盛線 |  |  | Y目盛線
| #DIV/0! | [13 empty] | BEEの分子側(Q) |  | #DIV/0! | 0 |  | 50 | 50 |  | 0 | 100
[15 empty] | 0 | #VALUE! | #VALUE! | 0.1 |  | 0 | 100 |  | 50 | 50
[15 empty] | 0 | 0 | #DIV/0! | #DIV/0!
Standard calculation
[15 empty] | BEE | X | 0 | 16.6667 | 33.3333 | 50 | 66.6667 | 83.3333 | 100
[16 empty] | S | 100 | 100 | 100 | 100 | 100 | 100 | 100
[15 empty] | 3 | A | 50 | 50 | 100 | 100 | 100 | 100 | 100
[15 empty] | 1.5 | B+ | 0 | 25 | 50 | 75 | 100 | 100 | 100
[15 empty] | 1 | B | 0 | 16.6667 | 33.3333 | 50 | 66.6667 | 83.3333 | 100
[15 empty] | 0.5 | B- | 0 | 8.3333 | 16.6667 | 25 | 33.3333 | 41.6667 | 50
[15 empty] | Rank(green star) | #DIV/0! | #DIV/0! | Standard calculation | ④上記+ オフサイト手法 | Standard calculation | This chart indicates rough estimate of lifecycle CO2 emission from subject building compared with that from reference building.
[6 empty] | This chart indicates rough estimate of lifecycle CO2 emission from subject building compared with that from reference building. | [8 empty] | (blank star) | #DIV/0! |  | Individual calculation |  | Individual calculation | This chart indicates rough estimate of lifecycle CO2 emission calculated by the assessor (individual calculation) from subject building compared with that from reference building. Refer "LCCO2 calculation conditions sheet (individual calculation)" to see the assumptions for the conditions
[15 empty] | LCCO2(kg-CO2/ym2) | Construction | Repair, renewal/demolition | Operation | On-site | Off-site | % | Sum
2-4 Assessment results of Medium-level categories (bar chart) | [14 empty] | Ref | 0 | 0 | 0 |  |  | 100% | 0
Q Environmental Quality | [10 empty] | Score of Q= | #DIV/0! |  |  | Subjest1 | 0 | 0 | 0 |  |  | #DIV/0! | 0 | N.A.
| Q1 Indoor Environment |  |  |  |  | Q2 Quality of Service |  |  |  | Q3 Outdoor Environment on Site |  |  |  |  | Subjest2 |  |  |  | 0 |  | #DIV/0! | 0 | N.A.
[5 empty] | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  | Subjest3 |  |  |  |  | 0 | #DIV/0! | 0 | N.A.
[16 empty] | Score(Round Down) | Score |  | Score(Round Down) | Score |  | Score(Round Down) | Score
[15 empty] | Q1 Indoor Environment | #DIV/0! | #DIV/0! | Q2 Quality of Service | #DIV/0! | #DIV/0! | Q3 Outdoor Environment on Site | #DIV/0! | #DIV/0!
[16 empty] | Score(Round Down) | NA |  | Score(Round Down) | NA |  | Score(Round Down) | NA
[15 empty] | Noise & Acoustics | #DIV/0! | #DIV/0! | Service Ability | #DIV/0! | #DIV/0! | Preservation & Creation of Biotope | 3
[15 empty] | Thermal Comfort | #DIV/0! | #DIV/0! | Durability & Reliability | #DIV/0! | #DIV/0! | Townscape & Landscape | 3
[15 empty] | Lighting & Illumination | #DIV/0! | #DIV/0! | Flexibility & Adaptability | #DIV/0! | #DIV/0! | Local Characteristics & Outdoor Amenity | #DIV/0! | #DIV/0!
LR 環境負荷低減性 | [10 empty] | Score of LR= | #VALUE! |  |  | Air Quality | #DIV/0! | #DIV/0!
| LR1 Energy Energy |  |  |  |  | LR2 Resources & Materials |  |  |  | LR3 Off-site Environment
[5 empty] | #VALUE! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0!
[16 empty] | Score(Round Down) | Score |  | Score(Round Down) | Score |  | Score(Round Down) | Score
[15 empty] | LR1 Energy | #VALUE! | #VALUE! | LR2 Resources & Materials | #DIV/0! | #DIV/0! | LR3 Off-site Environment | #DIV/0! | #DIV/0!
[16 empty] | Score(Round Down) | NA |  | Score(Round Down) | NA |  | Score(Round Down) | NA
[15 empty] | Building Thermal Load | #VALUE! | #VALUE! | Service Ability | #DIV/0! | #DIV/0! | Global Warming | 0 | N.A.
[15 empty] | Natural Energy Utilization | #DIV/0! | #DIV/0! | Durability & Reliability | #DIV/0! | #DIV/0! | Local environment | #DIV/0! | #DIV/0!
[15 empty] | Efficiency in Building Service System | 0 | N.A. | Flexibility & Adaptability | #DIV/0! | #DIV/0! | Surrounding Environment | #DIV/0! | #DIV/0!
[15 empty] | Efficient Operation | #DIV/0! | #DIV/0!
3 Design considerations
General | [9 empty] | Other
Describe briefly comprehensive concept of environmental design of the building. | [9 empty] | Describe briefly considerations for other than 6 categories above that is not assessed in CASBEE-NC, such as recycling activities at constriction site and preservation of historic buildings.
Q1 Indoor Environment | [5 empty] | Q2 Quality of Service |  |  |  | Q3 Outdoor Environment on Site
Describe briefly considerations for Q1 Indoor Environment of the building. | [5 empty] | Describe briefly considerations for Q2 Quality of Service of the building. |  |  |  | Describe briefly considerations for Q3 Outdoor Environment on Site of the building.
LR1 Energy | [5 empty] | LR2 Resources & Materials |  |  |  | LR3 Off-site Environment
Describe briefly considerations for LR1 Energy of the building. | [5 empty] | Describe briefly considerations for LR2 Resources & Materials of the building. |  |  |  | Describe briefly considerations for LR3 Off-site Environment of the building.
（3） 建築物の総合的な環境性能とは別枠の重要評価項目 | [12 empty] | 注3
（3）-1 建築物の代表的な環境負荷に関する定量的な評価指標 | [12 empty] | ＜実施設計段階、竣工段階で詳細な評価を行う場合に記入＞
|  |  | 年間延床面積あたり指標 |  |  | 人・時間あたり指標 |  | 年間延床面積あたり削減量 |  | 削減率 ％ |  |  | %
| 運用エネルギー消費量 |  |  | ＭＪ/年㎡ |  |  | ＭＪ/人時 |  | ＭＪ/年㎡
| 運用CO2排出量 |  |  | kg-CO2/年㎡ |  |  | kg-CO2/人時 |  | kg-CO2/年㎡
| 水消費量 |  |  | m3/年㎡ |  |  | m3/人時 |  | m3/年㎡
| LCCO2排出量 |  |  | kg-CO2/年㎡ |  |  | kg-CO2/人時 |  | kg-CO2/年㎡
| LC廃棄物量 |  |  | ｔ/年㎡ |  |  | ｔ/人時 |  | ｔ/年㎡
| LC資源消費量 |  |  | ｔ/年㎡ |  |  | ｔ/人時 |  | ｔ/年㎡
（3）-2 デザインプロセスの評価
設計段階 | [7 empty] | 建設段階
| 有資格者による設計 | [6 empty] | 環境管理計画
| 凡例 Q： | Quality | L：Load |  |  | LR：Load Reduction |  | SQ：Score of Q category |  | SLR：Score of LR category |  | BEE：Building Environmental Efficiency
| 備考 注1： | 当該対象区における標準的な計画の得点が３点。ＮＡは評価対象外とした項目を示す。敷地選定に関わる評価は対象外。
| 注2： | Qは、環境品質・性能（Q）のスコアSQ(Q-1、Q-2、Q-3のスコアにそれぞれの重み係数を乗じた合計値）から算定。
Lは、環境負荷低減性（LR)のスコアSLR（LR-1、LR-2、LR-3のスコアにそれぞれの重み係数を乗じた合計値）から算定。
| 注3： | (3)の評価はオプションとし、実施設計段階および竣工段階で可能な範囲で記入する。
BEE =
S: ★★★★★ A: ★★★★ B+: ★★★ B-: ★★ C: ★
30%: ☆☆☆☆☆ 60%: ☆☆☆☆ 80%: ☆☆☆ 100%: ☆☆ over 100%: ☆
1.Reference value
2.Building-related initiatives
3.Above initiatives + other on-site measures
4.Above initiatives + other off-site measures
（ kg-CO2/yr-m2 ）
Score of Q3 =
Score of Q2 =
Score of Q1 =
Score of LR3 =
Score of LR2 =
Score of LR1 =
n CASBEE: Comprehensive Assessment System for Built Environment Efficiency
n Q: Quality (building environmental quality); L: Load (building environmental load); LR: Load Reduction (environmental load reduction of the building); BEE: Built Environment Efficiency
n "Lifecycle CO2" is the total carbon dioxide emitted by a building during its entire life from the production of members and construction of the building to occupation by the users, repairs, and demolition/disposal.
n Calculation of LCCO2 for a building is normally a very large task, but for CASBEE it can be found simply through an approximate calculation. Specifically, we have set a base LCCO2 emission volume for each building type, so that it can be calculated almost automatically from the results (scoring levels) of assessment items related to CO2 emissions.
n For lifecycle CO2 calculation conditions, refer to the Manual and the Lifecycle CO2 Calculation Sheet.
Noise &
Acoustics
Thermal
Comfort
Lighting &
Illumination
Air Quality
Service
Ability
Durability
& Reliability
Flexibility
& Adaptability
Preservation & Creation of Biotope
Townscape & Landscape
Local Characteristics & Outdoor Amenity
Building Thermal Load
Natural
Energy Utilization
Efficiency in Building Service
System
Efficient Operation
System
Water Resources
Reduction of
Non Renewable
Material use
Materials with
Low Health
Risks
Global Warming
Local environment
Surrounding Environment

## Score
CASBEE for Building (New Construction) 2014 Edition | [8 empty] | n Manual: | CASBEE for Building (New Construction) 2014 Edition | [19 empty] | ■使用評価マニュアル： |  |  | CASBEE for Building (New Construction) 2014 Edition |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校
XXX Building | [5 empty] | Enter figures and comments. |  |  | n Software: | CASBEE-BD_NCe_2014(v.2.1) | [19 empty] | ■評価ソフト： |  |  | CASBEE-BD_NCe_2014(v.2.1) |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Score Sheet | [13 empty] | 採点シートの 採点結果 | [6 empty] | 建物全体・共用部分 | 住居・宿泊部分 | 用途別スコア入力 |  |  |  |  | ↓Q1とQ2の1は対象外の為、入力不要です。
|  |  |  | Summary of environmentally conscious efforts in design |  |  |  |  | Entire Building and Common Properties |  | Residential and Accomodation sections |  |  |  |  | 建物全体 |  | 住居宿泊 |  |  | #DIV/0! | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 学校 (小中高) | 病院 | ホテル | 集合住宅 | 建物全体・共用部分 |  |  | 面積加重 |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 学校 (小中高) | 病院 | ホテル | 集合住宅
Concerned categories | [8 empty] | Score | weighｔ | Score | weighｔ | Total | 建物全体 | 住居宿泊 | 解説シートの 採点結果 | 重み 係数 | 解説シートの 採点結果 | 重み 係数 | 全体 | weight(set) | weight(set) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 評価点 | 重み 係数 | 全体 | 評価点 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Q Environmental Quality of the building | [12 empty] | #DIV/0! | [6 empty] | #DIV/0! | 0 | 0 | [12 empty] | #DIV/0! | #DIV/0!
Q1 Indoor Environment | [9 empty] | #DIV/0! |  | 0 | #DIV/0! |  |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [11 empty] | #DIV/0! | #DIV/0! | #DIV/0!
1 | Noise & Acoustics | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 0 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.1 | Noise | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Background noise level | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Equipment noise | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
| 1.2 | Sound Insulation | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Sound Insulation of Openings | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Sound Insulation of Partition Walls | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 3 | Sound Insulation Performance of Floor Slabs (light-weight impact source) | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 4 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
| 1.3 | Sound Absorption | [6 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
2 | Thermal Comfort | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 0 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.1 | Room Temperature Control | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Room Temperature Setting | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Variable Loads and Following-up Control | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Perimeter Performance | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | Zoned Control | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 5 | Temperature and Humidity Control | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 6 | Individual Control | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  | 0 |  | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 7 | Allowance for After-hours Air Conditioning | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 8 | Monitoring Systems | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.2 | Humidity Control | [6 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.3 | Type of Air Conditioning System | [6 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | [6 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | [6 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
3 | Lighting & Illumination | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 0 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.1 | Daylighting | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Daylight Factor | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Openings by Orientation | [5 empty] | 0 | #DIV/0! | 3 | #DIV/0! |  |  | 3 |  | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | Daylight Devices | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.2 | Anti-glare Measures | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Glare from Light Fixtures | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Daylight Control | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | 映り込み対策 | [5 empty] | 0 |  |  |  |  | 0 |  | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.3 | Illuminance Level | [6 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | 照度 | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | 照度均斉度 | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.4 | Lighting Controllability | [6 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
4 | Air Quality | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 0 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.1 | Source Control | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Chemical Pollutants | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Asbestos | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 3 | Mites, Mold etc | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 4 | Legionella | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0!
| 4.2 | Ventilation | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Ventilation Rate | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Natural Ventilation Performance | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 3 | Consideration for Outside Air Intake | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 4 | Air Supply Planning | [5 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0!
| 4.3 | Operation Plan | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | CO2 Monitoring | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Control of Smoking | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
Q2 Quality of Service | [8 empty] | 0 | #DIV/0! | 0 | 0 | #DIV/0! |  |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [11 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Service Ability | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 5 |  |  |  |  | 0 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.1 | Functionality & Usability | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Provision of Space & Storage | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Use of Advanced Information System | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | Barrier-free Planning | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 1.2 | Amenity | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Perceived Spaciousness & Access to View | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Space for Refreshment | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | Décor Planning | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 1.3 | Maintenance Management | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Design Which Considers Maintenance Management | [5 empty] | #DIV/0! | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Securing Maintenance Management Functions | [5 empty] | #DIV/0! | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | [6 empty] | #DIV/0! | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
2 | Durability & Reliability | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 4 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 2.1 | Earthquake Resistance | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Earthquake-resistance | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Seismic Isolation & Vibration Damping Systems | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.2 | Service Life of Components | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Service Life of Structural Frame Materials | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Necessary Refurbishment Interval for Exterior Finishes | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | Necessary Renewal Interval for Main Interior Finishes | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 4 | Necessary Replacement Interval for Air Conditioning and Ventilation Ducts | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 5 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 6 | Necessary Renewal Interval for Major Equipment and Services | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.3 | Appropriate renewal | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.4 | Reliability | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | HVAC System | [5 empty] | #DIV/0! | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Water Supply & Drainage | [5 empty] | #DIV/0! | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | Electrical Equipment | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 4 | Support Method of Machines & Ducts | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 5 | Communications & IT Equipment | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
[9 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | #DIV/0! | 0 | [10 empty] | 0
3 | Flexibility & Adaptability | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 3 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 3.1 | Spatial Margin | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Allowance for Floor-to-floor Height | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Adaptability of Floor Layout | [5 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
| 3.2 | Floor Load Margin | [6 empty] | 3 | #DIV/0! | 3 | #DIV/0! |  | 3 | 3 | 3 | #DIV/0! | 3 | #DIV/0! |  | #DIV/0! | #DIV/0!
| 3.3 | Adaptability of Facilities | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Ease of Air Conditioning Duct Renewal | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Ease of Water Supply and Drain Pipe Renewal | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 3 | Ease of Electrical Wiring Renewal | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 4 | Ease of Communications Cable Renewal | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 5 | Ease of Equipment Renewal | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 6 | Provision of Backup Space | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
Q3 Outdoor Environment on Site | [8 empty] | 0 | #DIV/0! | 0 | 0 | #DIV/0! |  |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [11 empty] | #DIV/0! | #DIV/0! | #DIV/0!
1 | Preservation & Creation of Biotope | [7 empty] | 3 | #DIV/0! | 0 | #DIV/0! | 3 | 3 |  | 3 | #DIV/0! |  | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 3 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | Townscape & Landscape | [7 empty] | 3 | #DIV/0! | 0 | #DIV/0! | 3 | 3 |  | 3 | #DIV/0! |  | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 3 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
3 | Local Characteristics & Outdoor Amenity | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 3 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 3.1 | Attention to Local Charcter & Improvement of Comfort | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
| 3.2 | Improvement of the Thermal Environment on Site | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
[9 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | #DIV/0! | 0
LR Environmental Load Reduction of the building | [8 empty] | 0 | 0 | 0 | 0 | #VALUE! |  |  |  | 0 |  |  | #VALUE! | #DIV/0! | #DIV/0! | [12 empty] | #VALUE! | #VALUE!
LR1 Energy | Energy | [7 empty] | 0 | #VALUE! | 0 | 0 | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE! | #DIV/0! | #DIV/0! | [11 empty] | #VALUE! | #VALUE! | #VALUE!
1 | Building Thermal Load | [7 empty] | #VALUE! | #VALUE! | 0 | #DIV/0! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | [10 empty] | #VALUE! | #VALUE! |  | #VALUE! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Natural Energy Utilization | [7 empty] | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 3 |  |  |  |  | #DIV/0! | #VALUE! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[9 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 自然エネルギー利用 | [6 empty] | 0 | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
[9 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
[9 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
3 | Efficiency in Building Service System |  |  | BEIm | Non-residential | 1 | Apt (residential area) | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 |  | 0 | #VALUE! | 0 | 0 | 0 | #DIV/0! | #DIV/0! | [10 empty] | 0 | #VALUE! |  | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other than apartment (3a.3b) | [6 empty] | 3 | #DIV/0! | 0 | 0 |  | 3 |  | 3 | #DIV/0! |  | 0 |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | Apartment (3c) | [6 empty] | 0 | #DIV/0! | 0 | 0 |  | 0 |  | 0 | #DIV/0! |  | 0 |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.1 | 空調設備 | [6 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.2 | 換気設備 | [6 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.3 | 照明設備 | [6 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.4 | 給湯設備 | [6 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.5 | 昇降機設備 | [6 empty] | 0 | #DIV/0! | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 3.6 | エネルギー利用効率化設備 | [6 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  | 0 |  | #DIV/0! | #DIV/0! | [10 empty] | 0
4 | Efficient Operation | [7 empty] | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 3 |  |  |  |  | #DIV/0! | #VALUE! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  | Other than apartments | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 4.1 | Monitoring | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0!
|  | 4.2 | Operation & Management System | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0!
|  | Apartments | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 4.1 | Monitoring | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0!
|  | 4.2 | Operation & Management System | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0!
LR2 Resources & Materials | [8 empty] | 0 | #VALUE! | 0 | 0 | #DIV/0! |  |  |  | #VALUE! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [11 empty] | #VALUE! | #DIV/0! | #DIV/0!
1 | Water Resources | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 4 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 1.1 | Water Saving | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 1.2 | Rainwater & Gray Water | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Rainwater Use System | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Gray Water Reuse System | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
2 | Reducing Usage of Non-renewable Resources | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 4 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 2.1 | Reducing Usage of Materials | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.2 | Continuing Use of Existing Building Skeleton etc | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.3 | Use of Recycled Materials as Structural Frame Materials |  | 0 |  |  |  |  | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.4 | Use of Recycled Materials as Non-structural Materials |  | 0 |  |  |  |  | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.5 | Timber from Sustainable Forestry | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.6 | Reusability of Components and Materials | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
3 | Avoiding the Use of Materials with Pollutant Content | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 4 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 3.1 | Use of Materials without Harmful Substances | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
| 3.2 | Avoidance of CFCs and Halons | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Fire Retardant | [5 empty] | 4 | #DIV/0! | 0 | #DIV/0! |  | 4 |  | 4 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Insulation Materials | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 3 | Refrigerants | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
LR3 Off-site Environment | [8 empty] | 0 | #VALUE! | 0 | 0 | #DIV/0! |  |  |  | #VALUE! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [11 empty] | #VALUE! | #DIV/0! | #DIV/0!
1 | Consideration of Global Warming | [7 empty] | 0 | #DIV/0! | 0 | #DIV/0! | 0 | 0 |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0! | #DIV/0! | [5 empty] | 4 |  |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | Consideration of Local Environment | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 4 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 2.1 | Air Pollution | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.2 | Heat Island Effect | [6 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
| 2.3 | Load on Local Infrastructure | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 1 | Reduction of Rainwater Discharge Loads | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 2 | Sewage Load Suppression | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 3 | Traffic Load Control | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | [10 empty] | 0
|  | 4 | Waste Treatment Loads | [5 empty] | 3 | #DIV/0! | 0 | 0 |  | 3 |  | 3 | #DIV/0! |  | 0 |  | #DIV/0! | 0 | [10 empty] | 0
3 | Consideration of Surrounding Environment | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 |  |  |  |  | 4 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| 3.1 | Noise, Vibration & Odor | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Noise | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Vibration | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 3 | Odor | [5 empty] | 3 | #DIV/0! | 0 | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
| 3.2 | Wind Damage & Sunlight Obstruction | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Restriction of Wind Damage | [5 empty] | 3 | #DIV/0! |  | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Restriction of Sand and Dust | [5 empty] | 3 | #DIV/0! |  |  |  | 3 |  | 3 | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
|  | 3 | Restriction of sunlight obstruction | [5 empty] | 3 | #DIV/0! |  | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
| 3.3 | Light Pollution | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 1 | Outdoor Illumination and Light that Spills from Interiors | [5 empty] | 3 | #DIV/0! |  | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
|  | 2 | Measures for Reflected Solar Glare from Building Walls | [5 empty] | 3 | #DIV/0! |  | #DIV/0! |  | 3 |  | 3 | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
Note on M126: 専有部と共用部(3aによる評価)の床面積による加重平均

## Consider
n Considerations in environmental design |  | n Building Name | XXX Building
Considerations in design
General | Describe briefly comprehensive concept of environmental design of the building.
Q1 Indoor Environment | Describe briefly considerations for Q1 Indoor Environment of the building.
Q2 Quality of Service | Describe briefly considerations for Q2 Quality of Service of the building.
Q3 Outdoor Environment on Site | Describe briefly considerations for Q3 Outdoor Environment on Site of the building.
LR1 Energy | Describe briefly considerations for LR1 Energy of the building.
LR2 Resources & Materials | Describe briefly considerations for LR2 Resources & Materials of the building.
LR3 Off-site Environment | Describe briefly considerations for LR3 Off-site Environment of the building.
Other | Describe briefly considerations for other than 6 categories above that is not assessed in CASBEE-NC, such as recycling activities at constriction site and preservation of historic buildings.
Note on E3: 計画上の配慮事項：100字以内で記述してください。

## Coefficient
Emissions Coefficient
Emissions coefficient for electricity use (for Standard Calculation) |  |  |  |  | Published Actual/adjusted CO2 emission coefficients per PPS in 2012 |  |  |  | 1 | ←オプションボタン番号
| PPS/Reason, etc. | CO2 emission coefficient |  |  |  | Coefficient per PPS and alterative value based on Ordinance on Calculations of GHG Emissions
| Provide evidence | N.A. | (t-CO2/kWh) |  | [1] Actual emission coefficient
[6 empty] | Hokkaido Electric Power Co., Inc. | 0.000688 |  | ↓事業社名 | ↓排出係数
[6 empty] | Tohoku Electric Power Co., Inc. | 0.0006 |  | 0 | 0
(1) Using a designated emission coefficient: | [5 empty] | Tokyo Electric Power Co., Inc. | 0.000525
| PPS/Reason, etc. | CO2 emission coefficient |  |  |  | Chubu Electric Power Co., Inc. | 0.000516 |  | N.A.
|  |  | (t-CO2/kWh) |  |  | Hokuriku Electric Power Co., Inc. | 0.000663
[6 empty] | Kansai Electric Power Co., Inc. | 0.000514
(2) Using a coefficient based on the calculation method for GHG emissions as referred to in the Basic Law for Prevention of Global Warming: | [5 empty] | Chugoku Electric Power Co., Inc. | 0.000738
A. | Electricity supplied by general and specified power producers/suppliers (PPS) |  |  |  |  | Shikoku Electric Power Co., Inc. | 0.0007
[6 empty] | Kyushu Electric Power Co., Inc. | 0.000612
| Name of PPS | CO2 emission coefficient |  |  |  | Okinawa Electric Power Co., Inc. | 0.000903
|  | #N/A | (t-CO2/kWh) |  |  | eREX Co., Ltd. | 0.000603
[6 empty] | Idemitsu Green Power Co., Ltd. | 8.6e-05
B. | Other |  |  |  |  | Itochu Enex Co., Ltd. | 0.000676
| PPS/Reason, etc. | CO2 emission coefficient |  |  |  | Eneserve Corp. | 0.000616
|  |  | (t-CO2/kWh) |  |  | Ebara Environmental Plant Co., Ltd. | 0.000456
[6 empty] | Oji Paper Co., Ltd. | 0.000475
C. | Alternative coefficient value |  |  |  |  | ORIX Corp. | 0.000762
| Reasons, etc. | CO2 emission coefficient |  |  |  | e-sell Co.,Ltd. | 0
| Alternative value |  | (t-CO2/kWh) |  |  | Ennet Corp. | 0.000429
[6 empty] | F-Power Co., Ltd. | 0.000525
(3) Other than above: | [5 empty] | G-Power Co., Ltd. | 0.000441
| PPS/Reason, etc. | CO2 emission coefficient |  |  |  | Nihon Ceremony Corp. | 0.000797
|  |  | (t-CO2/kWh) |  |  | Summit Energy Corp. | 0.000438
[6 empty] | JX Nippon Oil & Energy Corp. | 0.000367
[6 empty] | J JEN Holdings Co., Ltd. | 0.000494
[6 empty] | Shigakogen Resort Kaihatsu Corp. | 0.000312
[6 empty] | Showa Shell Sekiyu K.K. | 0.000367
[6 empty] | Nippon Steel & Sumikin Engineering Co, Ltd. | 0.000655
[6 empty] | Senboku Natural Gas Power Generation Co., Ltd. | 0.000388
[6 empty] | Diamond Power Corp. | 0.000431
[6 empty] | Tess Engineering Co.,Ltd. | 0.000494
[6 empty] | Tokyo Eco Service Co., Ltd. | 9.2e-05
[6 empty] | Nihon Techno Co., Ltd. | 0.000508
[6 empty] | Japan Logistic Coop. | 0.000486
[6 empty] | Panasonic Corp. | 0.000498
[6 empty] | Premium Green Power Corp. | 1.8e-05
[6 empty] | Marubeni Corp. | 0.000378
[6 empty] | Mitsuuroko Green Energy Co., Ltd. | 0.000366
[6 empty] | Les Power Co.,Ltd. | 0.00042 | (t-CO2/kWh)
[2] Alternative coefficient
[6 empty] | Alternative value | 0.00055 | (t-CO2/kWh)
降順並び替え |  | Actual emissions coefficient/ Alternative coefficient |  | Adjusted emission coefficient
| Chubu Electric Power Co., Inc. | 0.000516 |  | 0.000373 |  | 調整後排出係数 | N.A.
| Chugoku Electric Power Co., Inc. | 0.000738 |  | 0.000672 |  | 実排出係数との差 | #N/A
| Diamond Power Corp. | 0.000431 |  | 0.000427
| Ebara Environmental Plant Co., Ltd. | 0.000456 |  | 0.000456
| Eneserve Corp. | 0.000616 |  | 0.000482
| Ennet Corp. | 0.000429 |  | 0.000427
| eREX Co., Ltd. | 0.000603 |  | 0.000428
| e-sell Co.,Ltd. | 0 |  | 0
| F-Power Co., Ltd. | 0.000525 |  | 0.000445
| G-Power Co., Ltd. | 0.000441 |  | 0
| Hokkaido Electric Power Co., Inc. | 0.000688 |  | 0.00068
| Hokuriku Electric Power Co., Inc. | 0.000663 |  | 0.000494
| Idemitsu Green Power Co., Ltd. | 8.6e-05 |  | 0.000106
| Itochu Enex Co., Ltd. | 0.000676 |  | 0.000293
| J JEN Holdings Co., Ltd. | 0.000494 |  | 0.00049
| Japan Logistic Coop. | 0.000486 |  | 0.000256
| JX Nippon Oil & Energy Corp. | 0.000367 |  | 0.000364
| Kansai Electric Power Co., Inc. | 0.000514 |  | 0.000475
| Kyushu Electric Power Co., Inc. | 0.000612 |  | 0.000599
| Les Power Co.,Ltd. | 0.00042 |  | 0
| Marubeni Corp. | 0.000378 |  | 0.000324
| Mitsuuroko Green Energy Co., Ltd. | 0.000366 |  | 0.000445
| Nihon Ceremony Corp. | 0.000797 |  | 0.000789
| Nihon Techno Co., Ltd. | 0.000508 |  | 0.000509
| Nippon Steel & Sumikin Engineering Co, Ltd. | 0.000655 |  | 0.000654
| Oji Paper Co., Ltd. | 0.000475 |  | 0.000471
| Okinawa Electric Power Co., Inc. | 0.000903 |  | 0.000692
| ORIX Corp. | 0.000762 |  | 0.000757
| Panasonic Corp. | 0.000498 |  | 0.000492
| Premium Green Power Corp. | 1.8e-05 |  | 2.2e-05
| Senboku Natural Gas Power Generation Co., Ltd. | 0.000388 |  | 0.000385
| Shigakogen Resort Kaihatsu Corp. | 0.000312 |  | 0.000309
| Shikoku Electric Power Co., Inc. | 0.0007 |  | 0.000656
| Showa Shell Sekiyu K.K. | 0.000367 |  | 0.000364
| Summit Energy Corp. | 0.000438 |  | 0.000259
| Tess Engineering Co.,Ltd. | 0.000494 |  | 0.00049
| Tohoku Electric Power Co., Inc. | 0.0006 |  | 0.00056
| Tokyo Eco Service Co., Ltd. | 9.2e-05 |  | 9.1e-05
| Tokyo Electric Power Co., Inc. | 0.000525 |  | 0.000406

## Q1
[11 empty] | n Building Name | XXX Building |  | プルダウン選択肢
|  | Q1 Indoor Environment | [5 empty] | Select from pull-down menus or enter figures and comments. | [5 empty] | <N.A.> |  |  | Preliminary design stage
[15 empty] | Yes | ON | Execution design stage
|  | 1 | Sound Environment | [13 empty] | Construction completion stage
|  | 1.1 | Noise | [9 empty] | dB(A) |  |  |  | 0
|  |  |  | 1.1.1 室内騒音レベル |  |  |  | #DIV/0! |  |  |  |  | dB(A)
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! |  | Residential and Accommodation Sections |  | Weighting coefficients (default) = | #DIV/0!
|  |  |  | 3 | Off,Hsp(Waiting Room),Htl,Fct,Apt | Sch(Univ.,etc), Hsp(Examining Room) | Rtl,Rst | Hal | Sch(ES/JS/JHS) | 3 | Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 50 < [Background noise level] | 45 < [Background noise level] | 55 < [Background noise level] | 40 < [Background noise level] | 60 < [Background noise level] | Level 1 | 45 < [Background noise level] |  |  |  | 1 | Level 1 | ■Level 1
2 | - |  |  | Level 2 | (No corresponding level) | (No corresponding level) | (No corresponding level) | (No corresponding level) | 50 < [Background noise level] ≦ 60 | Level 2 | (No corresponding level) |  |  |  | 2 | Level 2 | ■Level 2
3 | 3 |  |  | ■Level 3 | 45 < [Background noise level] ≦ 50 | 40 < [Background noise level] ≦ 45 | 50 < [Background noise level] ≦ 55 | 35 < [Background noise level] ≦ 40 | 45 < [Background noise level] ≦ 50 | ■Level 3 | 40 < [Background noise level] ≦ 45 |  |  |  | 3 | Level 3 | ■Level 3
4 | 4 |  |  | Level 4 | 40 < [Background noise level] ≦ 45 | 35 < [Background noise level] ≦ 40 | 45 < [Background noise level] ≦ 50 | 30 < [Background noise level] ≦ 35 | 35 < [Background noise level] ≦ 45 | Level 4 | 35 < [Background noise level] ≦ 40 |  |  |  | 4 | Level 4 | ■Level 4
5 | 5 |  |  | Level 5 | [Background noise level] ≦ 40 | [Background noise level] ≦ 35 | [Background noise level] ≦ 45 | [Background noise level] ≦ 30 | [Background noise level] ≦ 35 | Level 5 | [Background noise level] ≦ 35 |  |  |  | 5 | Level 5 | ■Level 5
0 | 0 |  |  | Noise: Allowable indoor noise levels | [10 empty] | 0 | レベル | レベル
|  |  |  | dB (A) | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
|  |  |  | NC-NR | 10～15 | 15～20 | 20～25 | 25～30 | 30～35 | 35～40 | 40～45 | 45～50 | 50～55
|  |  |  | Intrusiveness | 20: Silent―――; 25: ―――――――――Very Quiet―――――――――; 40: ―Not significantly noticeable――――――; 50: Perceived noise―; 55: ――――――Noise cannot be ignored
|  |  |  | Impact on | 30: A whispering voice is audible from 5m away; 40: Possible from 10m apart; 50: Possible from 3m apart; 60: Loud conversation (3m)
|  |  |  | conversation | 40: Telephone use (normal); 45: ――――――; 50: Telephone use (bearable); 55: ――――――; 60: Telephone use (unbearable)
|  |  |  | Studios | Silent room | Announcement | Radio studio | Television studios | Miximg room | General offices
|  |  |  | Venues and halls | 25: studio
|  |  |  | Hospitals | 25: Music hall; 30: Theater (medium); 35: Stage theaters; 40: Movie theater; 50: Hotel lobbies
|  |  |  | Hotels and | 40: and planetarium
|  |  |  | residentials |  | Hearing test | Special sickrooms | Operating rooms and bedrooms | Examining room | Laboratories | Waiting rooms
|  |  |  | General offices | 25: room
|  |  |  | Public buildings | 35: Reading rooms; 40: Bedrooms; 45: Banquet halls; 50: Lobbies
|  |  |  | Schools and churches | 35: Executive rooms; 40: Reception rooms; 45: Meeting rooms; 60: Typing and accounting rooms
|  |  |  | Commercial buildings | 35: and large meeting rooms
Refer to Architectural Institute of Japan, Handbook of Building Environmental Design 1 - Environment, 1978. P13
|  |  |  | 1.1.2 設備騒音対策 | 35: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Apt居,宿泊部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | #DIV/0! | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct（2000㎡未満） |  | #DIV/0! | Hsp,Htl | Hsp,Htl（2000㎡未満） | Apt
|  |  |  | #DIV/0! | 騒音対策を行っていない（Efforts to be evaluatedにおいてなんら取組みがない） |  | 騒音対策を行っていない（Efforts to be evaluatedにおいてなんら取組みがない） |  | #DIV/0! | 騒音対策を行っていない（Efforts to be evaluatedにおいてなんら取組みがない） | 騒音対策を行っていない（Efforts to be evaluatedにおいてなんら取組みがない） | 騒音対策を行っていない（Efforts to be evaluatedにおいてなんら取組みがない）
|  |  |  | #DIV/0! | 20: 若干の対策を行っている（Efforts to be evaluatedにおいて2項目以上を採用）; 30: 若干の対策を行っている（Efforts to be evaluatedにおいて1項目以上を採用）; 40: #DIV/0!; 45: 若干の対策を行っている（Efforts to be evaluatedにおいて2項目以上を採用）; 50: 若干の対策を行っている（Efforts to be evaluatedにおいて1項目以上を採用）
|  |  |  | #DIV/0! | 対策を行っている（Efforts to be evaluatedにおいて4項目以上を採用） |  | 対策を行っている（Efforts to be evaluatedにおいて2項目以上を採用） |  | #DIV/0! | 対策を行っている（Efforts to be evaluatedにおいて4項目以上を採用） | 対策を行っている（Efforts to be evaluatedにおいて2項目以上を採用） | 対策を行っている（Efforts to be evaluatedにおいて2～3項目以上を採用）
|  |  |  | #DIV/0! | 20: やや高度な対策を行っている（Efforts to be evaluatedにおいて6項目以上を採用）; 30: やや高度な対策を行っている（Efforts to be evaluatedにおいて3項目以上を採用）; 40: #DIV/0!; 45: やや高度な対策を行っている（Efforts to be evaluatedにおいて6項目以上を採用）; 50: やや高度な対策を行っている（Efforts to be evaluatedにおいて3項目以上を採用）
|  |  |  | #DIV/0! | 高度な対策を行っている（Efforts to be evaluatedにおいて全ての項目を採用） |  | 高度な対策を行っている（Efforts to be evaluatedにおいて全ての項目を採用） |  | #DIV/0! | 高度な対策を行っている（Efforts to be evaluatedにおいて全ての項目を採用） | 高度な対策を行っている（Efforts to be evaluatedにおいて全ての項目を採用） | 高度な対策を行っている（Efforts to be evaluatedにおいて全ての項目を採用）
A.Apt宅以外の建築Rtlにおける設備騒音対策のEfforts to be evaluated
2,000㎡未満の基準で評価する。
|  |  |  | .建Rtl全体,共用部分 | 20: Apt居,宿泊部分
|  |  |  | 0 | 20: 0; 25: ← 直接入力; 30: ON
1 | 1 |  |  | 0 | 0 | 設備騒音の種類 |  | 対策例 |  | 延床面積 | 0 | Apt居,宿泊部分 | 0
2 | 2 |  |  |  | 25: 吹出し口、吸込み口からの騒音; 35: 低騒音型吹出し口、低騒音型吸込み口、位置、風量,風速の適正化など
3 | 3 |  |  | Yes | 20: Yes; 25: 室内空調機からの騒音; 35: 防音カバー、位置など
4 | 4 |  |  |  | 20: Yes; 25: 機械室からの騒音（透過騒音）; 35: 防音カバー、機械室の吸音,遮音、位置など; 45: 2,000㎡未満の建築Rtl
5 | 5 |  |  | Yes | 25: 同上（固体伝搬音）; 35: 防振架台、防振支持など; 45: 設備騒音の種類; 55: 対策例
0 | 0 |  |  | Yes | 25: ダクト,配管からの騒音（透過騒音）; 35: 消音ダクト、消音エルボ、消音ボックス、防音管巻き、位置など; 45: 配管からの騒音（透過騒音）; 55: 防音管巻き、位置など
|  |  |  | Yes | 25: 同上（固体伝搬音）; 35: 防振吊り、防振支持、フレキシブルジョイント、貫通部の防振施Fctなど; 45: 同上（固体伝播音）; 55: 防振吊り、防振支持、フレキシブルジョイント、貫通部の防振施Fctなど
[5 empty] | Yes | （屋外）冷却塔、室外機等からの騒音 |  | 防音塀、遮蔽体、防振支持、位置など |  | ビルマルチエアコン室内機等からの騒音 |  | 低騒音タイプの機器の採用など
|  |  |  | Yes | 20: Yes; 25: （屋外）吸込み口,排気口からの騒音; 35: 位置、風量,風速の適正化など; 45: ビルマルチエアコン室外機等からの騒音; 55: 防音塀、遮蔽体、防振支持、位置など
|  |  |  | 5 | 20: 4; 25: 項目
B．Apt宅における設備騒音対策のEfforts to be evaluated
[5 empty] | 0 | ← 直接入力 | ON
1 | 1 |  |  |  | 20: 0; 25: Apt宅; 35: Apt居,宿泊部分; 40: 0
2 | 2 |  |  |  | 25: 設備騒音の種類; 35: 対策例
3 | 3 |  |  |  | 20: Yes; 25: トイレ、浴室等の給配水音、排水音、使用音; 35: 適正な水圧、防音管巻き、管の防振支持金具、便器の防振支持、浴室の防振支持、位置など
4 | 4 |  |  |  | 20: Yes; 25: ウォーターハンマー; 35: 適正な水圧、ウォーターハンマー防止器の採用など
5 | 5 |  |  |  | 25: エアコン室内機等からの騒音; 35: 低騒音タイプの機器の採用など
0 | 0 |  |  |  | 25: エアコン室外機からの騒音; 35: 防振ゴム、防振マット、低騒音タイプの機器
[5 empty] | Yes | 換気扇からの騒音 |  | 低騒音タイプの機器の採用など
[5 empty] | 3 | 項目
|  | 1.2 | Sound Insulation
|  |  |  | 1.2.1 Sound Insulation of Openings | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 3; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
- | - |  |  | Level 1 | 20: 騒音が気になる。; 40: Level 1; 45: 騒音が気になる。
3 | 3 |  |  | Level 2 | 40: Level 2
- | - |  |  | Level 3 | 20: 騒音がほとんど気にならない。; 40: Level 3; 45: 騒音がほとんど気にならない。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 騒音が気にならない; 40: Level 5; 45: 騒音が気にならない。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | 20: Less than T-1; 40: Level 1; 45: Lower than T-1
|  |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
|  |  |  | ■Level 3 | 20: T-1; 40: ■Level 3; 45: T-1
|  |  |  | Level 4 | 20: (No corresponding level); 40: Level 4; 45: (No corresponding level)
|  |  |  | Level 5 | 20: T-2 or above; 40: Level 5; 45: T-2 or higher
|  |  |  | 1.2.2 Sound Insulation of Partition Walls | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rst,Fct; 30: Hsp（Examining Room）; 40: 3; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 人の話し声が気になる。; 30: Hal話等の話の内容がわかる。; 40: Level 1; 45: テレビ、ラジオ、Hal話等の一般の発生音がかなり聞こえる。; 55: 隣戸の生活がかなり分かる。
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: 人の話し声が気にならない。; 30: Hal話等の一般の発生音が小さく聞える。; 40: Level 3; 45: テレビ、ラジオ、Hal話等の一般の発生音が小さく聞こえる。; 55: 隣戸Apt宅の生活がわかるがあまり気にならない。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 人の話し声がほとんど聞こえない。; 30: Hal話等の一般の発生音がほとんど聞えない。; 40: Level 5; 45: テレビ、ラジオ、Hal話等の一般の発生音が通常では聞こえない。; 55: 隣戸の気配を感じない。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | 20: Less than Dr-30; 30: Less than Dr-35; 40: Level 1; 45: Less than Dr-40
|  |  |  | Level 2 | 20: Dr-30; 30: Dr-35; 40: Level 2; 45: Dr-40
|  |  |  | ■Level 3 | 20: Dr-35; 30: Dr-40; 40: ■Level 3; 45: Dr-45
|  |  |  | Level 4 | 20: Dr-40; 30: Dr-45; 40: Level 4; 45: Dr-50
|  |  |  | Level 5 | 20: Dr-45 or more; 30: Dr-50 or more; 40: Level 5; 45: Dr-55 or more
|  |  |  | 1.2.3 Sound Insulation Performance of Floor Slabs (light-weight impact source) | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Sch; 40: 3; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 椅子の移動音、Rtlの落下音がかなりうるさい。; 40: Level 1; 45: 椅子の移動音、Rtlの落下音がかなり気になる。
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: 椅子の移動音、Rtlの落下音がかなり気になる。; 40: Level 3; 45: 椅子の移動音、Rtlの落下音が小さく聞こえる。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 椅子の移動音、Rtlの落下音が小さく聞こえる。; 40: Level 5; 45: 椅子の移動音、Rtlの落下音がほとんど聞こえない。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | 20: Worse than Lr-65; 40: Level 1; 45: Worse than Lr-55
|  |  |  | Level 2 | 20: Lr-65; 40: Level 2; 45: Lr-55
|  |  |  | ■Level 3 | 20: Lr-60; 40: ■Level 3; 45: Lr-50
|  |  |  | Level 4 | 20: Lr-55; 40: Level 4; 45: Lr-45
|  |  |  | Level 5 | 20: Lr-50 or better; 40: Level 5; 45: Lr-40 or better
|  |  |  | 1.2.4 Sound Insulation Performance of Floor Slabs (heavy-weight impact source) | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Sch; 40: 3; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 人のとびはねや走り回る音がうるさい。; 40: Level 1; 45: 人のとびはねや走り回る音がかなり気になる。
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: 人のとびはねや走り回る音がよく聞こえる。; 40: Level 3; 45: 人のとびはねや走り回る音が聞こえる。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 人のとびはねや走り回る音が小さく聞こえる。; 40: Level 5; 45: 人のとびはねや走り回る音が聞こえるが意識することはあまりない。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | 20: Worse than Lr-65; 40: Level 1; 45: Worse than Lr-60
|  |  |  | Level 2 | 20: Lr-65; 40: Level 2; 45: Lr-60
|  |  |  | ■Level 3 | 20: Lr-60; 40: ■Level 3; 45: Lr-55
|  |  |  | Level 4 | 20: Lr-55; 40: Level 4; 45: Lr-50
|  |  |  | Level 5 | 20: Lr-50 or better; 40: Level 5; 45: Lr-45 or better
|  | 1.3 | Sound Absorption |  | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct; 40: 3; 45: Hsp,Htl
1 | 1 |  |  | Level 1 | 20: Sound absorbing materials are not used; 40: Level 1; 45: Sound absorbing materials are not used
- | - |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Sound absorbing materials are used in one of the following areas; 40: ■Level 3; 45: Sound absorbing materials are used in one of the following areas
4 | 4 |  |  | Level 4 | 20: (walls, floor or ceiling); 40: Level 4; 45: (walls, floor or ceiling)
5 | 5 |  |  | Level 5 | 20: Sound absorbing materials are used in two of the following areas; 40: Level 5; 45: Sound absorbing materials are used in two of the following areas
0 | 0
|  | 2 | Thermal Comfort
|  | 2.1 | Room Temperature Control
|  |  |  | 2.1.1 Room Temperature | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 50: Residential and Accommodation Sections; 55: Weighting coefficients (default) =; 60: #DIV/0!
|  |  |  | 3 | Off | Hsp(Waiting Room),Htl,Fct,Apt | Hsp(Examining Room) | Sch(Univ.,etc) | Sch（ES/JS/JHS） | Rtl,Rst,Hal | 3 | Hsp,Htl | Apt
1 | 1 | bar: 20 to 45; 55 to 60
2 | 2 |  |  | Level 1 | レベル２を満たさない。 | 冬期20℃、夏期28℃と多少我慢を強いる室温設定。 | 冬期21℃、夏期28℃と程度と多少我慢を強いる室温設定。 | 冬期10℃以上、夏期30℃以下と多少我慢を強いる室温設定。 | (該当するレベルなし) | 冬期18℃、夏期28℃程度と多少我慢を強いる室温設定。 | Level 1 | 冬期20℃、夏期28℃と多少我慢を強いる室温設定。 | 各室において冬期18℃、夏期28℃程度を強いる設定としている。
3 | 3 |  |  | Level 2 | 20: 冬期20℃、夏期28℃と多少我慢を強いる室温設定。; 40: (該当するレベルなし); 50: Level 2
4 | 4 |  |  | Level 3 | 一般的な冬期22℃、夏期26℃の設定。 | 一般的な冬期22℃、夏期26℃の設定。 | 一般的な冬期23℃、夏期26℃の設定。 | 一般的な冬期18～20℃、夏期25～28℃の設定。 | 冬期18℃以上、夏期28℃以下の範囲を設定している。 | 一般的な冬期20℃、夏期26℃の設定。 | Level 3 | 一般的な冬期22℃、夏期26℃の設定。 | 各居室において一般的な冬期22℃、夏期26℃を設定している。
5 | 5 |  |  | Level 4 | 40: 冬期20℃以上 、夏期25℃以下の設定。; 50: Level 4
0 | 0 |  |  | Level 5 | ASHRAE快適域やPOEM-Oを参考に冬期22℃～24℃、夏期24℃～26℃の範囲を設定している。 |  |  |  | 冬期22℃以上、夏期24℃以下の設定。 | ASHRAE快適域やPOEM-Oを参考に冬期20℃～22℃、夏期24℃～26℃の範囲を設定している。 | Level 5 | ASHRAE快適域やPOEM-Oを参考に冬期22℃～24℃、夏期24℃～26℃の範囲を設定している。 | 各居室において冬期22～24℃、夏期24～26℃の範囲を設定している。
[5 empty] | 実施,竣Fct | [6 empty] | 実施,竣Fct
|  |  |  | Level 1 | Not adequate for Level 2. | Minimum equipment capacity to achieve room temperatures of 20˚C in winter and 28˚C in summer with some occupant discomfort | Minimum equipment capacity to achieve room temperatures of 21˚C in winter and 28˚C in summer with some occupant discomfort | The minimum equipment capacity is provided to achieve temperatures of 10˚C or more in winter and 30˚C or less in summer, which require tolerance of some discomfort | (No corresponding level) | Minimum equipment capacity to achieve room temperatures of 18˚C in winter and 28˚C in summer with some occupant discomfort | Level 1 | Minimum equipment capacity to achieve room temperatures of 20˚C in winter and 28˚C in summer with some occupant discomfort | Minimum equipment capacity to achieve room temperatures of 18˚C in winter and 28˚C in summer with some occupant discomfort
|  |  |  | Level 2 | 20: Minimum equipment capacity to achieve temperatures of 20˚C in winter and 28˚C in summer with some occupant discomfort; 40: (No corresponding level); 50: Level 2
|  |  |  | ■Level 3 | Sufficient equipment capacity to achieve a general room temperatures of 22˚C in winter and 26˚C in summer | Sufficient equipment capacity to achieve a general room temperatures of 22˚C in winter and 26˚C in summer | Sufficient equipment capacity to achieve a general room temperature of 23˚C in winter and 26˚C in summer | Sufficient equipment capacity for achieving commonly-applied room temperatures of 20˚C in winter and 27˚C in summer | Minimum equipment capacity to achieve room temperatures of 18˚C or higher in winter and 28˚C or lower in summer | Sufficient equipment capacity to achieve general room temperatures of 20˚C in winter and 26˚C in summer | ■Level 3 | Sufficient equipment capacity to achieve general room temperatures of 22˚C in winter and 26˚C in summer
|  |  |  | Level 4 | 40: Sufficient equipment capacity to achieve room temperatures of 20˚C or higher in winter and 25˚C or lower in summer; 50: Level 4
|  |  |  | Level 5 | 20: Sufficient equipment capacity to achieve room temperatures of 24˚C in both winter and summer; 40: Sufficient equipment capacity to achieveg room temperatures of 22˚C or higher in winter and 24˚C or lower in summer; 45: Sufficient equipment capacity to achieve room temperatures of 22˚C in winter and 24˚C in summer; 50: Level 5; 55: Sufficient equipment capacity to achieve room temperature of 24˚C in both winter and in summer
|  |  |  | 2.1.2 負荷変動,追従制御性 | 35: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!
|  |  |  | 0 | 20: Sch,Rtl,Rst,Hal
1 | 1 |  |  | Level 1 | 20: 急激な負荷変動に対する考慮は特にしていない。
2 | 2 |  |  | Level 2
3 | 3 |  |  | Level 3 | 20: 一般的な負荷変動を考慮し、ある程度制御可能なシステムになっている。
4 | 4 |  |  | Level 4
5 | 5 |  |  | Level 5 | 20: 高度な負荷変動追従ができるような制御システムである。
0 | 0
|  |  |  | 2.1.2 Perimeter Performance | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 窓,外壁,屋根や床（特にピロティ）において室内への熱の侵入に対しての配慮が十分でなく、日射遮蔽性能や断熱性能が低い。; 40: Level 1; 45: 窓,外壁,屋根や床（特にピロティ）において室内への熱の侵入に対しての配慮が十分でなく、日射遮蔽性能や断熱性能が低い。; 55: 日本Apt宅性能表示基準「5-1断熱等性能等級」における等級1相当の屋根,外壁,床の部材構成、開口部の仕様を設定している。
3 | 3 |  |  | Level 2 | 40: Level 2; 55: 日本Apt宅性能表示基準「5-1断熱等性能等級」における等級2相当の屋根,外壁,床の部材構成、開口部の仕様を設定している。
4 | 4 |  |  | Level 3 | 20: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対しての配慮がなされており、実用上、日射遮蔽性能および断熱性能に問題がない。; 40: Level 3; 45: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対しての配慮がなされており、実用上、日射遮蔽性能および断熱性能に問題がない。; 55: 日本Apt宅性能表示基準「5-1断熱等性能等級」における等級3相当の屋根,外壁,床の部材構成、開口部の仕様を設定している。
5 | 5 |  |  | Level 4 | 40: Level 4; 55: (該当するレベルなし)
0 | 0 |  |  | Level 5 | 20: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対して、十分な配慮がなされており、最良の日射遮蔽性能および断熱性能を有する。; 40: Level 5; 45: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対して、十分な配慮がなされており、最良の日射遮蔽性能および断熱性能を有する。; 55: 日本Apt宅性能表示基準「5-1断熱等性能等級」における等級4相当の屋根,外壁,床の部材構成、開口部の仕様を設定している。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | 20: No attention has been paid to the infiltration of heat through window systems, outside walls, roof and floor (particularly where piloti are used), and insulation performance is poor. (Window system SC: around 0.7, U = 6.0 (W/m2K), outer walls and others: U = 3.0 (W/m2K)*1; 40: Level 1; 45: No attention has been paid to the infiltration of heat through window systems, outside walls, roof and floor (particularly where piloti are used), and insulation performance is poor. (Window system SC: around 0.7, U = 6.0 (W/m2K), outer walls and others: U = 3.0 (W/m2K)*1; 55: Requirements for Grade 1 in 5-1 Energy Saving Countermeasure Grade of the Japan Housing Performance Standard are satisfied.
|  |  |  | Level 2 | 40: Level 2; 55: Requirements for Grade 2 in 5-1 Energy Saving Countermeasure Grade of the Japan Housing Performance Standard are satisfied.
|  |  |  | ■Level 3 | 20: Attention has been paid to the infiltration of heat to the interior through windows, outside walls, roof and floor (particularly where piloti are used), and there is no practical problem with insolation blocking and insulation performance. (Window system SC: around 0.5, U = 4.0 (W/m2K), outer walls and others: U = 2.0 (W/m2K)*1; 40: ■Level 3; 45: Attention has been paid to the infiltration of heat to the interior through windows, outside walls, roof and floor (particularly where piloti are used), and there is no practical problem with insolation blocking and insulation performance. (Window system SC: around 0.5, U = 4.0 (W/m2K), outer walls and others: U = 2.0 (W/m2K)*1; 55: Requirements for Grade 3 in 5-1 Energy Saving Countermeasure Grade of the Japan Housing Performance Standard are satisfied.
|  |  |  | Level 4 | 40: Level 4; 55: (No corresponding level)
|  |  |  | Level 5 | 20: Close attention has been paid to the infiltration of heat to the interior through windows systems, outside walls, roof and floor (particularly where piloti are used), and the building has the highest level of insolation blocking and insulation performance. (Window system SC: around 0.2, U = 3.0 (W/m2K), outer walls and others: U = 1.0 (W/m2K)*1; 40: Level 5; 45: Close attention has been paid to the infiltration of heat to the interior through windows systems, outside walls, roof and floor (particularly where piloti are used), and the building has the highest level of insolation blocking and insulation performance. (Window system SC: around 0.2, U = 3.0 (W/m2K), outer walls and others: U = 1.0 (W/m2K)*1; 55: Requirements for Grade 4 in 5-1 Energy Saving Countermeasure Grade of the Japan Housing Performance Standard are satisfied.
|  |  |  | 2.1.3 Zoned Control | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 50: examples of HVAC systems
|  |  |  | 3 | 20: Off,Hsp,Htl,Fct; 35: Rtl,Rst,Hal
1 | 1 |  |  | Level 1 | 20: No distinction is made between orientation directions, or between perimeter and interior, and only one air conditioning system is planned*1, which must be switched between heating and cooling for each season; 35: There is no zoning of heating and cooling within a single floor, and a single-circuit air conditioning system is planned. Switching between heating and cooling is required for the selection of air conditioning modes.; 50: Single duct system, two-pipe FCU system (no zoning, switching between heating and cooling).
2 | 2 |  |  | Level 2
3 | 3 |  |  | ■Level 3 | 20: There are air conditioning zoning*1 that differentiates between orientation directions, between perimeter and interior, and between internal load distributions. The air conditioning system can provide either heating or cooling separately to each zone.; 35: Each floor is divided into multiple zones according to their thermal loads, and the air conditioning system is planned to allow either heating or cooling in each zone.; 50: Single duct system, two-pipe FCU system (zoning grade assessment, switching between heating and cooling).
4 | 4 |  |  | Level 4 | 20: There is air conditioning zoning at around the standard of level 3*1, and the system also allows selection between cooling and heating for each zone.; 35: There is air conditioning zoning at around the standard of level 3, and the planned system also allows selection between cooling and heating for each zone.; 50: Double duct system (4 pipes for AHU), four-pipe FCU system, task/ambient air conditioning system (evaluate both the zoning grade and simultaneous heating and cooling).
5 | 5 |  |  | Level 5 | 20: There are separate air conditioning systems for each orientation direction, and for perimeter and interior*1, allowing more detailed zoning (broadly, zones of 40 m2 or less). The air conditioning system can provide either heating or cooling separately to each zone.; 35: Each floor is divided into many small zones for individual sales areas or tenants, and the air conditioning system is planned to allow either heating or cooling in zone units.; 50: Multi-unit heat pump system (simultaneous heating and cooling), double duct system (4 pipes for AHU), and four-pipe FCU system level with more detailed zoning than levels 3 and 4 (zones of around 40 m2).
0 | 0
|  |  |  | 2.1.5 温度,湿度制御 | 35: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Apt居,宿泊部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 0; 45: Hsp,Htl
1 | 1 |  |  | Level 1 | 20: ＯＮ-ＯＦＦによる温度,湿度制御になっている。; 40: Level 1; 45: ＯＮ-ＯＦＦによる温度,湿度制御になっている。
2 | 2 |  |  | Level 2 | 20: 比例制御、多位置制御による温度,湿度制御になっている。; 40: Level 2; 45: 比例制御、多位置制御による温度,湿度制御になっている。
3 | 3 |  |  | Level 3 | 20: ＰＩＤ制御による温度,室内湿度になっている。; 40: Level 3; 45: ＰＩＤ制御による温度,室内湿度になっている。
4 | 4 |  |  | Level 4 | 40: Level 4
5 | 5 |  |  | Level 5 | 20: 快適センサーなどによる温度,湿度制御（快適範囲における温度制御）が可能である。; 40: Level 5; 45: 快適センサーなどによる温度,湿度制御（快適範囲における温度制御）が可能である。
0 | 0
|  |  |  | 2.1.6 個別制御 | 35: #DIV/0!
|  |  |  | Apt居,宿泊部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!
|  |  |  | 0 | 20: Hsp,Htl; 30: Apt
1 | 1 |  |  | Level 1 | 20: 在室者は手元で、Low-Middle-Highの風量切り替えが可能である。; 30: レベル３を満たさない。
2 | 2 |  |  | Level 2
3 | 3 |  |  | Level 3 | 20: 在室者は手元で、直接温度設定やLow-Middle-Highの風量調整が可能である。ただし、熱源側は季節に応じて冷暖切り替えである。; 30: 各室内で温度設定が可能。
4 | 4 |  |  | Level 4
5 | 5 |  |  | Level 5 | 20: 在室者は手元で、直接、温度設定や風量調整が可能である。（熱源側は冷暖同時）; 30: Apt戸内の温度を設定しつつ、各室において温度の個別設定が可能。
0 | 0
|  |  |  | 2.1.7 時間外空調に対する配慮 | 35: #DIV/0!; 40: 2.1.8 監視システム; 60: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: 建Rtl全体,共用部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Hsp,Htl,Fct; 40: 0; 45: Rtl,Rst
1 | 1 |  |  | Level 1 | 20: 時間外や休日時には、空調運転を行わない。; 40: Level 1; 45: 同一フロアで熱負荷別に複数にゾーニングがなされておらず、代表的なゾーン監視のためにセンサー等の監視システムが設置されている。
2 | 2 |  |  | Level 2 | 40: Level 2
3 | 3 |  |  | Level 3 | 20: 時間外や休日時には、居Apt者のフロア全体が空調可能なシステムとなっている。; 40: Level 3; 45: 同一フロアで熱負荷別に複数にゾーニングがなされており、複数ゾーン監視のために制御センサとは別に複数の監視,計測用センサがある監視システムが設置されている。
4 | 4 |  |  | Level 4 | 40: Level 4
5 | 5 |  |  | Level 5 | 20: 時間外や休日時には、居Apt者のゾーンのみ空調可能なシステムとなっている。; 40: Level 5; 45: 同一フロアで、売り場,テナント用に細かくゾーニングがなされており、それを細かく監視するために制御センサとは別に複数の監視,計測用センサがある監視システムが設置されている。
0 | 0
|  | 2.2 | Humidity Control |  | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | Off,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  | Sch(Univ.,etc) | Sch(ES/JS/JHS) | 3 | Hsp,Htl |  | Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | レベル３を満たさない。 |  | レベル３を満たさない。 | レベル３を満たさない。 | Level 1 | レベル３を満たさない。 |  | 何も配慮していない。
3 | 3 |  |  | Level 2 | 40: Level 2; 55: (該当するレベルなし)
4 | 4 |  |  | Level 3 | 加湿機能を有し、かつ一般的な冬期40％、夏期50％の設定で計画されている。 |  | 加湿機能を有し、かつ一般的な冬期40～70％、夏期50～65％。の範囲で計画されている。 | 一般的な冬期30～45％、夏期55％～80％の範囲で計画されている。 | Level 3 | 加湿機能を有し、かつ一般的な冬期40％、夏期50％の設定で計画されている。 |  | 適切な換気機能を有し、熱橋となる部分の断熱補強、防湿層、通気層の設置等の結露防止対策がとられている。
5 | 5 |  |  | Level 4 | 40: Level 4; 55: 除湿機能を有し、熱橋となる部分の断熱補強、防湿層、通気層の設置等の結露防止対策がとられている。
0 | 0 |  |  | Level 5 | 加湿,除湿機能を有し、かつASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 |  | 加湿,除湿機能を有し、ASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 | 加湿,除湿機能を有し、ASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 | Level 5 | 加湿,除湿機能を有し、かつASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 |  | 加湿,除湿機能を有し、45％～55％の快適範囲を設定し、なおかつ、熱橋となる部分の断熱補強、防湿層、通気層の設置等の結露防止対策がとられている。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | Not adequate for level 3. |  | Not adequate for level 3. | Not adequate for level 3. | Level 1 | Not adequate for level 3. |  | No consideration given.
|  |  |  | Level 2 | 40: Level 2; 55: (No corresponding level)
|  |  |  | ■Level 3 | Humidification equipment is available, and equipment capacity is generally sufficient to keep humidity to 50% in summer and 40% in winter.*1 |  | Humidification equipment is also available, and equipment capacity is generally sufficient to keep humidity to 40-70% in winter and 50-65% in summer. | Sufficient equipment capacity to achieve general indoor humidity of 30 to 45% in winter and 55 to 80% in summer. | ■Level 3 | Sufficient equipment capacity with humidifier to achieve general humidity of 50% in summer and 40% in winter. |  | Appropriate ventilation functions are provided, and anti-condensation measures have been taken on elements that can act as heat bridges, such as insulation reinforcement, humidity barriers and permeable layers.
|  |  |  | Level 4 | 40: Level 4; 55: Dehumidification functions are provided, and anti-condensation measures have been taken on elements that can act as heat bridges, such as insulation reinforcement, humidity barriers and permeable layers.
|  |  |  | Level 5 | Humidification and dehumidification equipment is available, and equipment capacity is sufficient to keep humidity in the range 45-55%.*2 |  | Humidification and dehumidification equipment is available, and equipment capacity is sufficient to keep humidity in the range 45-55%. | Sufficient equipment capacity with humidifier/dehumidifier to achieve humidity of 45 to 55%. | Level 5 | Humidification and dehumidification equipment is available, and equipment capacity is sufficient to keep humidity in the range 45-55%. |  | Dehumidification and humidification functions are provided and set to a comfort range of 45-55%, and anti-condensation measures have been taken on elements that can act as heat bridges, such as insulation reinforcement, humidity barriers and permeable layers.
|  | 2.3 | Type of Air Conditioning System |  | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp(Waiting Room),Htl,Fct,Apt; 30: Hsp(Examining Room); 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 居Apt域の上下温度差や気流速度について特に配慮していない空調方式が計画されている。; 30: 居Apt域の上下温度差や気流速度について特に配慮していない空調方式が計画されている。; 40: Level 1; 45: 居Apt域の上下温度差や気流速度について特に配慮していない空調方式が計画されている。; 55: 空調居Apt域の上下温度差、気流速度や非空調部屋との室間温度差などについて特に配慮していない空調方式が計画されている。
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: 通常の空調方式であるが、居Apt域の上下温度差や気流速度に配慮した給排気計画がなされている。; 30: 通常の空調方式であるが、居Apt域の上下温度差や気流速度およびExamining Room療室内の間仕切りなどに配慮した給排気計画がなされている。; 40: Level 3; 45: 通常の空調方式であるが、居Apt域の上下温度差や気流速度に配慮した給排気計画がなされている。; 55: 空調居Apt域の上下温度差、気流速度や非空調部屋との室間温度差などに配慮した空調方式が計画されている。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 居Apt域の上下温度差や気流速度が少なくなるように配慮された空調方式＊が採用されている。; 30: 居Apt域の上下温度差や気流速度が少なくなり、またExamining Room療室内の間仕切りに配慮された空調方式*が採用されている。; 40: Level 5; 45: 居Apt域の上下温度差や気流速度が少なくなるように配慮された空調方式＊が採用されている。; 55: 空調居Apt域の上下温度差、気流速度や非空調部屋との室間温度差などが少なくなるように配慮された空調方式が計画されている。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | 20: The air conditioning system was planned with no particular consideration for the vertical temperature distribution and airflow speed in occupancy zone.; 30: Air conditioning system designed without specific consideration of vertical temperature variation and air flow in occupied areas; 40: Level 1; 45: The air conditioning system was planned with no particular consideration for the vertical temperature distribution and airflow speed in occupancy zone.; 55: Air conditioning system designed without specific consideration of vertical temperature variation and air flow in air-conditioned occupied areas, or of temperature difference between air-conditioned and non-air-conditioned areas
|  |  |  | Level 2 | 40: Level 2
|  |  |  | ■Level 3 | 20: The air conditioning system is normal, but the air supply and extraction plan considered the vertical temperature distribution and airflow speed in occupancy zone.; 30: The air conditioning system is normal, but the air supply and extraction plan considered the vertical temperature distribution and airflow speed in occupancy zone, and the partitions in the medical examing rooms.; 40: ■Level 3; 45: The air conditioning system is normal, but the air supply and extraction plan considered the vertical temperature distribution and airflow speed in occupancy zone.; 55: Air conditioning system designed in consideration of vertical temperature variation and air flow in air-conditioned occupied areas, or of temperature difference between air- conditioned and non-air-conditioned areas
|  |  |  | Level 4 | 40: Level 4
|  |  |  | Level 5 | 20: The air conditioning system*1 was chosen to mitigate the vertical temperature distribution and airflow speed in the room.; 30: The air conditioning system*1 was chosen to mitigate the vertical temperature distribution and airflow speed in occupancy zone, and to consider the partitions of the medical examining rooms.; 40: Level 5; 45: The air conditioning system*1 was chosen to mitigate the vertical temperature distribution and airflow speed in occupancy zone.; 55: and non-air-conditioned areas
* This refers to, for example, ceiling and floor radiant heating and cooling systems, or floor-vented systems, etc.
|  |  |  | 2.3.1 上下温度差 | 35: #DIV/0!; 40: 2.3.2 平均気流速度; 60: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: 建Rtl全体,共用部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp（Waiting Room,Examining Room）,Htl,Fct,Apt; 40: 0; 45: Off,Sch,Rtl,Rst,Hal,Hsp（Waiting Room,Examining Room）,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | 20: 5℃＜ [上下温度差]; 40: Level 1; 45: 0.45ｍ/ｓ＜ [平均気流速度]
2 | 2 |  |  | Level 2 | 40: Level 2; 45: 0.35ｍ/ｓ＜ [平均気流速度] ≦0.45ｍ/ｓ
3 | 3 |  |  | Level 3 | 20: 2℃＜ [上下温度差] ≦5℃; 40: Level 3; 45: 0.25ｍ/ｓ＜ [平均気流速度] ≦0.35ｍ/ｓ
4 | 4 |  |  | Level 4 | 40: Level 4; 45: 0.15ｍ/ｓ＜ [平均気流速度] ≦0.25ｍ/ｓ
5 | 5 |  |  | Level 5 | 20: [上下温度差] ≦2℃; 40: Level 5; 45: [平均気流速度] ≦0.15ｍ/ｓ
0 | 0
|  | 3 | Lighting & Illumination
|  | 3.1 | Daylight
|  |  |  | 3.1.1 Daylight Factor | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Hsp,Htl,Fct,Apt; 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 |  |  | Level 1 | 20: [Daylight factor] < 1.0%; 40: Level 1; 45: [Daylight factor] < 0.5%; 55: [Daylight factor] < 0.5%
2 | 2 |  |  | Level 2 | 20: 1.0% ≦ [Daylight factor] < 1.5%; 40: Level 2; 45: 0.5% ≦ [Daylight factor] < 0.75%; 55: 0.5% ≦ [Daylight factor] < 1.0%
3 | 3 |  |  | ■Level 3 | 20: 1.5% ≦ [Daylight factor] < 2.0%; 40: ■Level 3; 45: 0.75% ≦ [Daylight factor] < 1.0%; 55: 1.0% ≦ [Daylight factor] < 1.5%
4 | 4 |  |  | Level 4 | 20: 2.0% ≦ [Daylight factor] < 2.5%; 40: Level 4; 45: 1.0% ≦ [Daylight factor] < 1.25%; 55: 1.5% ≦ [Daylight factor] < 2.0%
5 | 5 |  |  | Level 5 | 20: 2.5% ≦ [Daylight factor]; 40: Level 5; 45: 1.25% ≦ [Daylight factor]; 55: 2.0% ≦ [Daylight factor]
0 | 0
|  |  |  | 3.1.2 Openings by Orientation | 35: #DIV/0!
|  |  |  | Residential and Accommodation Sections | 30: Weighting coefficients(default) =; 35: #DIV/0!
|  |  |  | 3 | 20: Apt
1 | 1 |  |  | Level 1 | 20: No south-facing windows
- | 2 |  |  | Level 2 | 20: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: South-facing windows
- | 4 |  |  | Level 4 | 20: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: South and east-facing windows
0 | 0
|  |  |  | 3.1.3 Daylight Devices | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Fct; 30: Rtl,Rst,Hsp,Htl,Apt; 40: 3; 45: Hsp,Htl,Apt
- | - |  |  | Level 1 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 1; 45: (No corresponding level)
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: There are no daylight devices.; 30: There are no daylight devices.; 40: ■Level 3; 45: There are no daylight devices.
4 | - |  |  | Level 4 | 20: There is one type of daylight device.; 30: (No corresponding level); 40: Level 4; 45: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: There are two or more types of daylight device, or they have advanced functions.; 30: There are some daylight devices.; 40: Level 5; 45: There are some daylight devices.
0 | 0
|  | 3.2 | Anti-glare Measures
|  |  |  | 3.2.1 照明器具のグレア | 35: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Apt居,宿泊部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Hsp,Htl,Fct,Apt; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: 水平方向から見て光源が露出し、グレアを制限していない器具。G3分類の器具。; 40: Level 1; 45: 水平方向から見て光源が露出しグレアを制限していない器具。G3分類の器具。
- | - |  |  | Level 2 | 20: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 水平方向から見て光源が露出せず、グレアを制限している器具。G2分類の器具。; 40: Level 3; 45: 水平方向から見て光源が露出せずグレアを制限している器具。G2分類の器具。
- | - |  |  | Level 4 | 20: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし)
5 | 5 |  |  | Level 5 | 20: 反射板形状のFct夫、ルーバー,透光性カバーなどにより、十分にグレアを制限している器具。G1、G0、V分類の器具。; 40: Level 5; 45: 反射板形状のFct夫、ルーバー,透光性カバーなどにより十分にグレアを制限している器具。G1、G0、V分類の器具。
0 | 0
|  |  |  | 3.2.1 Daylight Control | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch(Univ.,etc),Hsp,Htl,Fct,Apt; 30: Sch（ES/JS/JHS）; 40: 3; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: Nothing.; 30: Nothing.; 40: Level 1; 45: Nothing.
2 | - |  |  | Level 2 | 20: Glare control using screens, awnings and eaves.; 30: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Glare is controlled with blinds, or by a combination of any two among screens, awnings and eaves.; 30: Glare control using screens, awnings and eaves.; 40: ■Level 3; 45: Glare control using curtains, screens, awnings and eaves.
4 | 4 |  |  | Level 4 | 20: Glare is controlled with blinds, together with any of one among screens, awnings and eaves.; 30: Glare control using blinds or any combination of two or more fixtures including curtains, screens, awnings and eaves; 40: Level 4; 45: Glare is controlled with blinds, or a combination of any two among curtains, screens, awnings and eaves.
5 | 5 |  |  | Level 5 | 20: Glare is controlled by automatically-controlled blinds.; 30: Glare control using blinds and at least one other fixture, including curtains, screens, awnings and eaves; 40: Level 5; 45: Glare is controlled with blinds, together with any of one among curtains, screens, awnings and eaves.
0 | 0
|  |  |  | 3.2.2 Reflection Control | 35: #DIV/0!
既存 |  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!
|  |  |  | 0 | 20: Sch（ES/JS/JHS）
1 | 1 |  |  | Level 1 | 20: レベル３を満たさない。
- | 2 |  |  | Level 2 | 20: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 教室内で視界に見え方を妨害するような「まぶしさ」を感じさせる強い光源がないこと。 （解説（ア）～（ウ））
- | 4 |  |  | Level 4 | 20: (該当するレベルなし)
5 | 5 |  |  | Level 5 | 20: レベル３を満たし、かつ、カーテンを使用する、などの運用面の取り組みを行っている。
0 | 0 |  |  |  | 20: 判定表
[5 empty] | 評価項目 | 判定基準
[5 empty] | （ア） | 児童生徒等から見て、黒板の外側15°以内の範囲に輝きの強い光源（昼光の場合は窓）がない。
[5 empty] | （イ） | 見え方を妨害するような光沢が、黒板及び机上面にない。
[5 empty] | （ウ） | 見え方を妨害するような電灯や明るい窓等が、テレビ及びコンピュータ等の画面に映じていない。
|  | 3.3 | Illuminance Level |  | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 50: Residential and Accommodation Sections; 55: Weighting coefficients (default) =; 60: #DIV/0!
|  |  |  | 3 | Off,Hsp(Examining Room),Fct |  | Sch | Hsp(Waiting Room) | Htl | Apt | 3 | Hsp | Htl,Apt
1 | 1 |  |  | Level 1 | (No corresponding level) |  | [Illuminance] < 300 lx | [Illuminance] < 150 lx | [Illuminance] < 100 lx | [Illuminance] < 100 lx | Level 1 | [Illuminance] < 150 lx | [Illuminance] < 100 lx
2 | - |  |  | Level 2 | [Illuminance] <300 lx, or 1,000 lx ≦ [Illuminance] |  | (No corresponding level) | (No corresponding level) | (No corresponding level) | (No corresponding level) | Level 2 | (No corresponding level) | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Overall lighting system: |  | 300 lx ≦ [Illuminance] < 500 lx, or 750 lx ≦ [Illuminance] | 150 lx ≦ [Illuminance] | 100 lx ≦ [Illuminance] | 100 lx ≦ [Illuminance] | ■Level 3 | 150 lx ≦ [Illuminance] | 100 lx ≦ [Illuminance]
4 | 4 |  |  | Level 4 | 300 lx ≦ [Illuminance] < 500 lx; |  | 500 lx ≦ [Illuminance] < 750 lx | Equivalent to level 3 and 100 lx ≦ [vertical illuminance] for walls | (No corresponding level) | Equivalent to level 3 and 100 lx ≦ [vertical illuminance] for walls | Level 4 | Equivalent to level 3 and a [vertical illuminance] for walls of 100 lx or higher | (No corresponding level)
5 | 5 |  |  | Level 5 | In cases of the task/ambient lighting system or its equivalent, and the task illuminance is more than 300 lx and less than 500 lx, or the ambient illuminance is less than 1/3 or more than 2/3 of the task illuminance |  | (No corresponding level) | (No corresponding level) | (No corresponding level) | (No corresponding level) | Level 5 | (No corresponding level) | Equivalent to level 3 and individual controls of multiple devices*1
0 | 0
|  |  |  | 3.3.2 照度均斉度 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: 建Rtl全体,共用部分; 40: 3; 45: Apt居,宿泊部分
[5 empty] | Off,Sch,Hsp(Examining Room),Htl,Fct,Apt |  |  |  |  | Hsp
|  |  |  | Level 1 | 20: 全般照明方式の場合で室内にかなり不快に感じる程度の非常に暗い部分がある。; 40: Level 1; 45: 全般照明方式の場合で室内にかなり不快に感じる程度の非常に暗い部分がある。
|  |  |  | Level 2 | 20: 全般照明方式の場合で室内にやや不快に感じる程度の暗い部分がある。; 40: Level 2; 45: 全般照明方式の場合で室内にやや不快に感じる程度の暗い部分がある。
|  |  |  | ■Level 3 | 20: 全般照明方式の場合で室内に許容できる程度の暗い部分がある。タスク,アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが不十分。; 40: ■Level 3; 45: 全般照明方式の場合で室内に許容できる程度の暗い部分がある。タスク,アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが不十分。
|  |  |  | Level 4 | 20: 全般照明方式の場合で室内にほとんど暗い部分がない。; 40: Level 4; 45: 全般照明方式の場合で室内にほとんど暗い部分がない。
|  |  |  | Level 5 | 20: 全般照明方式の場合で室内に暗い部分がない。タスク,アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが良い。; 40: Level 5; 45: 全般照明方式の場合で室内に暗い部分がない。タスク,アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが良い。
|  | 3.4 | Lighting Controllability |  | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch(Univ.,etc),Rtl,Hsp,Htl,Fct,Apt; 30: Sch(ES/JS/JHS); 40: 3; 45: Hsp; 55: Htl,Apt
1 | 1 | bar: 20 to 35; 45
- | - |  |  | Level 1 | 20: 照明制御ができない。; 30: 明るさやSch習形態に応じた制御区画ではない。; 40: Level 1; 45: 照明制御ができない。; 55: 照明制御ができない。
3 | 3 |  |  | Level 2 | 20: (該当するレベルなし); 30: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし); 55: (該当するレベルなし)
- | - |  |  | Level 3 | 20: 執務者,売り場等について複数単位の大まかな照明制御ができる。; 30: 明るさやSch習形態に応じた制御区画であり、在室者自らが点灯,消灯によって制御できる; 40: Level 3; 45: 複数ベッド単位の大まかな照明制御ができる。; 55: 室内で大まかな照明制御ができる。
5 | 5 |  |  | Level 4 | 20: (該当するレベルなし); 30: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし); 55: (該当するレベルなし)
0 | 0 |  |  | Level 5 | 20: 各執務者,売り場等の部分について、細かな照明制御ができる、または、自動照明制御ができる。; 30: レベル３を満たしている。かつ、部分的に自動調光ができる。; 40: Level 5; 45: ベッド単位の細かな照明制御ができる。; 55: 室内の複数部分に対して細かい照明制御ができる、または、自動照明制御ができる。
[5 empty] | 実施,竣Fct |  |  |  |  | 実施,竣Fct
|  |  |  | Level 1 | 20: Lighting control is not zoned and no control panel/devices are available for adjustment; 30: Lighting control is not zoned in accordance with illuminance levels and learning methods; 40: Level 1; 45: No lighting control is available; 55: No lighting control is available
|  |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level); 55: (No corresponding level)
|  |  |  | ■Level 3 | 20: Lighting control per four-task unit is available or control panel/devices are available for adjustment; 30: Lighting control is zoned in accordance with illuminance levels and learning methods, and on/off control by the occupants is available; 40: ■Level 3; 45: Lighting control per multi-bed unit is available or control panel/devices for adjustment are available; 55: Control panel/devices are available for broad lighting adjustment for the entire room
|  |  |  | Level 4 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 4; 45: (No corresponding level); 55: (No corresponding level)
|  |  |  | Level 5 | 20: Lighting control per task unit is available and adjustment via computer terminal/remote contol or automatic control is available; 30: Level 3 is satisfied and automatic lighting adjustment is partially available; 40: Level 5; 45: Detailed lighting control per bed is available; 55: Detailed lighting control per multi-zone unit is available via computer terminal/remote control OR automatic control system
|  | 4 | Air Quality
|  | 4.1 | Source Control
|  |  |  | 4.1.1 Chemical Pollutants | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 30: Sch（ES/JS/JHS）; 40: 3; 45: Hsp,Htl,Apt
- | - |  |  | Level 1 | 20: (No corresponding level); 40: Level 1; 45: (No corresponding level)
- | - |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Satisfies the Building Standard Law.; 40: ■Level 3; 45: Satisfies the Building Standard Law.
4 | 4 |  |  | Level 4 | 20: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 70% of the total area of floors, walls, ceilings and attics.; 40: Level 4; 45: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 70% of the total area of floors, walls, ceilings and attics.
5 | 5 |  |  | Level 5 | 20: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 90% of the total area of floors, walls, ceilings and attics; most material used has a low level of formaldehyde and other VOC emissions.; 40: Level 5; 45: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 90% of the total area of floors, walls, ceilings and attics; most material used has a low level of formaldehyde and other VOC emissions.
0 | 0
|  |  |  | 4.1.2 Asbestos | 35: #DIV/0!
既存のみ評価 |  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Apt居,宿泊部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル２を満たさない。; 40: Level 1; 45: レベル２を満たさない。
2 | 2 |  |  | Level 2 | 20: 吹き付けアスベスト等を使用しているが、封じ込め又は囲い込みが行われている。; 40: Level 2; 45: 吹き付けアスベスト等を使用しているが、封じ込め又は囲い込みが行われている。
3 | 3 |  |  | Level 3 | 20: 吹き付けアスベスト等を一切使用していない。; 40: Level 3; 45: 吹き付けアスベスト等を一切使用していない。
- | - |  |  | Level 4 | 20: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし)
- | - |  |  | Level 5 | 20: (該当するレベルなし); 40: Level 5; 45: (該当するレベルなし)
0 | 0
|  |  |  | 4.1.3 ダニ,カビ等 | 35: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Apt居,宿泊部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 30: Sch（ES/JS/JHS）; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル３を満たさない。; 30: レベル３を満たさない。; 40: Level 1; 45: レベル３を満たさない。
- | - |  |  | Level 2 | 20: (該当するレベルなし); 30: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 内装は、床,壁の50％以上～65％未満の面積において、ダニ,カビの発生を抑制、あるいは清掃,メンテナンスに配慮したものとなっている。; 30: ［ダニ又はダニアレルゲン］≦１００匹／㎡; 40: Level 3; 45: 内装は、床,壁の50％以上～65％未満の面積において、ダニ,カビの発生を抑制、あるいは清掃,メンテナンスに配慮したものとなっている。
4 | 4 |  |  | Level 4 | 20: 内装は、床,壁の65％以上～80％未満の面積において、ダニ,カビの発生を抑制、あるいは清掃,メンテナンスに配慮したものとなっている。; 30: (該当するレベルなし); 40: Level 4; 45: 内装は、床,壁の65％以上～80％未満の面積において、ダニ,カビの発生を抑制、あるいは清掃,メンテナンスに配慮したものとなっている。
5 | 5 |  |  | Level 5 | 20: 内装は、床,壁の80％以上の面積において、ダニ,カビの発生を抑制、あるいは清掃,メンテナンスに配慮したものとなっている。; 30: レベル３の基準に加え、定期的に掃除を行っている、などの運用面の取組を行っている。; 40: Level 5; 45: 内装は、床,壁の80％以上の面積において、ダニ,カビの発生を抑制、あるいは清掃,メンテナンスに配慮したものとなっている。
0 | 0
|  |  |  | 4.1.4 レジオネラ対策 | 35: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Apt居,宿泊部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Fct,Hsp; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル３を満たさない。; 40: Level 1; 45: レベル３を満たさない。
- | - |  |  | Level 2 | 20: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 冷却塔の水処理、飛散対策等が最低限施されており、給湯器も最低限の対策が施されている。; 40: Level 3; 45: 冷却塔の水処理、飛散対策等が最低限施されており、給湯器も最低限の対策が施されている。
4 | 4 |  |  | Level 4 | 20: 冷却塔がない。または、冷却塔の水処理、飛散対策等が十分に施されており、給湯器は最低限の対策が施されている。; 40: Level 4; 45: 冷却塔がない。または、冷却塔の水処理、飛散対策等が十分に施されており、給湯器は最低限の対策が施されている。
5 | 5 |  |  | Level 5 | 20: 確実な対策を行うために、レベル４を超える特別な配慮を行っている。かつ、それらの設備のメンテナンスが容易な計画となっている。; 40: Level 5; 45: 確実な対策を行うために、レベル４を超える特別な配慮を行っている。かつ、それらの設備のメンテナンスが容易な計画となっている。
0 | 0
|  | 4.2 | Ventilation |  | 20: #DIV/0!
|  |  |  | 4.2.1 Ventilation Rate | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch(Univ.,etc),Rtl,Rst,Hal, Hsp,Htl,Fct,Apt; 30: Sch（ES/JS/JHS）; 40: 3; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 30: (No corresponding level); 40: Level 1; 45: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 25 m3/h per person or higher; or if not centrally controlled, a ventilation rate as required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.; 30: Ventilation rate required in the Building Standard Law (including measures for sick house syndrome) and the School Sanitation Standards.; 40: ■Level 3; 45: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 25 m3/h per person or higher; or if not centrally controlled, a ventilation rate required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.
4 | 4 |  |  | Level 4 | 20: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 30 m3/h per person or higher; or if not centrally controlled, a ventilation rate 20% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.; 30: Ventilation rate that is 20% higher than required in the Building Standard Law (including measures for sick house syndrome) and the School Sanitation Standards.; 40: Level 4; 45: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 30 m3/h per person or higher; or if not centrally controlled, a ventilation rate 20% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.
5 | 5 |  |  | Level 5 | 20: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 35 m3/h per person or higher; or if not centrally controlled, a ventilation rate 40% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.; 30: Ventilation rate that is 40% higher than required in the Building Standard Law (including measures for sick house syndrome) and the School Sanitation Standards.; 40: Level 5; 45: For rooms equipped with a centrally-controlled air mixing system, aventilation rate of 35 m3/h per person or higher; or if not centrally controlled, a ventilation rate 40% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.
0 | 0
|  |  |  | 4.2.2 Natural Ventilation Performance | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch(Univ.,etc),Fct; 30: Sch（ES/JS/JHS）; 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 30: Not adequate for level 3.; 40: Level 1; 45: Not adequate for level 3.; 55: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level); 55: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Fixed windows and no valid opening for natural ventilation; or fixed windows and valid opening area for natural ventilation of less than 25 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/50 of the total floor space of an occupied room.; 30: Valid opening area for natural ventilation of at least 1/20 of the total floor space of an occupied room.; 40: ■Level 3; 45: Fixed windows and no valid opening for natural ventilation; or fixed windows and valid opening area for natural ventilation of less than 50 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/20 of the total floor space of an occupied room.; 55: Area of openable windows at least 1/10 of floor space of occupied room.
4 | 4 |  |  | Level 4 | 20: Fixed windows and valid opening area for natural ventilation of at least 25 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/30 of the total floor space of an occupied room; or where in-room air quality improvement is expected with use of outdoor air cooling system which can use more than double the required outdoor air volume.; 30: Valid opening area for natural ventilation of at least 1/15 of the total floor space of an occupied room.; 40: Level 4; 45: Fixed windows and valid opening area for natural ventilation of at least 50 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/15 of the total floor space of an occupied room; or where in-room air quality improvement is expected with use of outdoor air cooling system which can use more than double the required outdoor air volume.; 55: Area of openable windows at least 1/8 of floor space of occupied room.
5 | 5 |  |  | Level 5 | 20: Fixed windows and valid opening area for natural ventilation of at least 50 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/15 of the total floor space of an occupied room; or valid opening area for natural ventilation is equivalent to Level 4, and in-room air quality improvement is expected with use of outdoor air cooling system that can use more than double the required outdoor air volume.; 30: Valid opening area for natural ventilation of at least 1/10 of the total floor space of an occupied room.; 40: Level 5; 45: Fixed windows and valid opening area for natural ventilation of at least 100 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/10 of the total floor space of an occupied room; or valid opening area for natural ventilation is equivalent to Level 4, and in-room air quality improvement is expected with use of outdoor air cooling system that can use more than double the required outdoor air volume.; 55: Area of openable windows at least 1/6 of floor space of occupied room.
0 | 0
|  |  |  | 4.2.3 Consideration for Outside Air Intake | 35: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct; 30: Apt; 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 30: Not adequate for level 3.; 40: Level 1; 45: Not adequate for level 3.; 55: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level); 55: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.; 30: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site.; 40: ■Level 3; 45: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.; 55: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site.
4 | 4 |  |  | Level 4 | 20: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also positioned at least 6 m away from extraction vents.; 30: (No corresponding level); 40: Level 4; 45: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also positioned at least 6 m away from extraction vents.; 55: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents and positioned at least 6 m away.; 30: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.; 40: Level 5; 45: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents and positioned at least 6 m away.; 55: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.
0 | 0
|  |  |  | 4.2.4 給気計画 | 35: #DIV/0!
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Apt居,宿泊部分; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル３を満たさない。; 40: Level 1; 45: レベル３を満たさない。
- | - |  |  | Level 2 | 20: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 外気が空調機でレタンと混合され各室に熱負荷から決まる風量で配分される等、各室の負荷条件によっては、必ずしも必要な場所に必要な外気量が保証されないシステムとなっている。; 40: Level 3; 45: 外気が空調機でレタンと混合され各室に熱負荷から決まる風量で配分される等、各室の負荷条件によっては、必ずしも必要な場所に必要な外気量が保証されないシステムとなっている。
- | - |  |  | Level 4 | 20: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし)
5 | 5 |  |  | Level 5 | 20: 外気がレタンと混合されず、各室の必要外気量が直接各室に供給されている等、各室の負荷条件によらず、必要な場所に必要な外気量が保証されるシステムとなっている。; 40: Level 5; 45: 外気がレタンと混合されず、各室の必要外気量が直接各室に供給されている等、各室の負荷条件によらず、必要な場所に必要な外気量が保証されるシステムとなっている。
0 | 0
|  | 4.3 | Operation Plan
|  |  |  | 4.3.1 CO2 Monitoring | 35: #DIV/0!; 40: 4.3.2 Control of Smoking; 60: #DIV/0!
|  |  |  | Entire Building and Common Properties | 30: Weighting coefficients(default) =; 35: #DIV/0!; 40: Residential and Accommodation Sections; 55: Weighting coefficients(default) =; 60: #DIV/0!
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Fct; 40: 3; 45: Off,Sch,Rtl,Rst,Hal,Hsp(Waiting Room),Htl,Fct
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 40: Level 1; 45: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: The system is based on manual measurement, with the minimum necessary level of recording.; 40: ■Level 3; 45: There is a minimum level of measures, such as smoking booths, to avoid exposing non-smokers to smoke.
4 | - |  |  | Level 4 | 20: The system is based on manual measurement, a management manual, etc. has been provided for properly maintaining air quality, and it functions effectively.; 40: Level 4; 45: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: The system has constant central monitoring of CO2. Also, a management manual, etc. has been provided for properly maintaining air quality, and it functions effectively.; 40: Level 5; 45: Smoking is confirmed to be prohibited in the entire building. Alternatively, there is an adequate level of measures, such as smoking booths, to avoid exposing non-smokers to smoke.
0 | 0

## Q2
[11 empty] | n Building Name | XXX Building |  | プルダウン選択肢
|  | Q2 Quality of Service | [5 empty] | Select from pull-down menus or enter figures and comments. | [5 empty] | <評価しない> | Yes |  | Preliminary design stage
[16 empty] | ON | Execution design stage | 特定建築Rtlに該当する場合の取組みで評価する
|  | 1 | Service Ability | [13 empty] | Construction completion stage
|  | 1.1 | Functionality & Usability | [11 empty] | はい |  | 0
|  |  |  | 1.1.1 Provision of Space & Storage |  |  |  | #DIV/0! | [6 empty] | いいえ
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! | Residential and Accommodation Sections |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Fct |  |  |  | 3 | Hsp |  | Htl
1 | 1 |  |  | Level 1 | Not adequate for level 3. |  |  |  | Level 1 | Not adequate for level 3. |  | Not adequate for level 3. |  |  | 1 | Level 1 | ■Level 1
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level) |  | (No corresponding level) |  |  | 2 | Level 2 | ■Level 2
3 | 3 |  |  | ■Level 3 | Working space* per person is at least 6 m2. |  |  |  | ■Level 3 | Private rooms at least 8 m2/bed, multi-bed rooms at least 6 m2/bed. |  | Single room at least 15 m2, twin room at least 22 m2. |  |  | 3 | Level 3 | ■Level 3
4 | 4 |  |  | Level 4 | Working space* per person is at least 9 m2. |  |  |  | Level 4 | (No corresponding level) |  | Single room at least 22 m2, twin room at least 32 m2. |  |  | 4 | Level 4 | ■Level 4
5 | 5 |  |  | Level 5 | Working space* per person is at least 12 m2 |  |  |  | Level 5 | Private rooms at least 10 m2/bed, multi-bed rooms at least 8 m2/bed. |  | Single room at least 30 m2, twin room at least 40 m2. |  |  | 5 | Level 5 | ■Level 5
0 | 0 | [13 empty] | 0 | レベル | レベル
|  |  |  | 1.1.2 Use of Advanced Information System |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! | Residential and Accommodation Sections |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Fct |  |  |  | 3 | Htl,Apt
1 | 1 |  |  | Level 1 | Not adequate for level 2. |  |  |  | Level 1 | Not adequate for level 2.
2 | 2 |  |  | Level 2 | Measures such as OA floors* accommodate layout changes, and electrical sockets for OA equipment have at least 30 VA/m2 socket capacity. In addition, optical fiber is routed into the building for communications. |  |  |  | Level 2 | Communications lines able to carry telephone and broadcasting are routed into each dwelling or guest room.
3 | 3 |  |  | ■Level 3 | Measures such as OA floors accommodate layout changes, and electrical sockets for OA equipment have at least 30 VA/m2 socket capacity. Also, level 2 is satisfied for communications, and communications lines with capacity for one data communications device per 8 m2 (one phone, one PC) is routed onto each floor. |  |  |  | ■Level 3 | Level 2 is satisfied, and Internet services not adequate for level 4 are provided.
4 | 4 |  |  | Level 4 | Measures such as OA floors accommodate layout changes, and electrical sockets for OA equipment have at least 40 VA/m2 socket capacity. Also, level 3 is satisfied for communications, lines for multiple communications carriers are routed into the building, and space is provided for each communications carrier to lay cables onto each floor. |  |  |  | Level 4 | Each dwelling or guest room is equipped with a communications environment able to use 100 Mbit-class broadband.
5 | 5 |  |  | Level 5 | Measures such as OA floors accommodate layout changes, and electrical sockets for OA equipment have at least 50 VA/m2 socket capacity. Also, level 4 is satisfied for communications, Gigabit communications lines are routed onto each floor, and tenant EPS is ensured for communications between floors. |  |  |  | Level 5 | Each dwelling or guest room is equipped with a communications environment able to use Gbit-class broadband.
0 | 0
|  |  |  | 1.1.3 Barrier-free Planning |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Rtl,Rst,Hal,Hsp,Htl |  |  |  | Off,Sch,Fct,Apt |  | Rtl,Rst,Hal,Hsp,Htl [<2000m2]
1 | 1 |  |  | Level 1 | Not adequate for level 3. |  |  |  | Not adequate for level 3.
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | (No corresponding level)
3 | 3 |  |  | ■Level 3 | The building satisfies the standard for easing building use (the minimum level) under the New Barrier-free Building Law. |  |  |  | At least half of the building satisfies the standard for easing building use (the minimum level) under the New Barrier-free Building Law.
4 | 4 |  |  | Level 4 | The building satisfies the standard for easing building use (the preferred level) under the New Barrier-free Building Law. |  |  |  | The building satisfies the standard for easing building use (the minimum level) under the New Barrier-free Building Law.
5 | 5 |  |  | Level 5 | The building exceeds the standard for easing and guiding building use (the preferred level) under the New Barrier-free Building Law, achieving the universal design level. |  |  |  | The building satisfies the standard for easing building use (the desirable level) under the New Barrier-free Building Law.
0 | 0
|  | 1.2 | Amenity
|  |  |  | 1.2.1 Perceived Spaciousness & Access to View |  |  |  | #DIV/0!
既存はOff務所のみ評価 |  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! |  |  | Residential and Accommodation Sections | Weighting coefficients (default) = | #DIV/0!
|  |  |  | 3 | Off,Fct |  | Rtl,Rst |  | Sch(Univ.,etc) | Sch（ES/JS/JHS） | 3 | Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | Not adequate for level 3. |  | Not adequate for level 3. |  | Not adequate for level 2. | Not adequate for level 3. | Level 1 | Not adequate for level 3.
2 | - |  |  | Level 2 | (No corresponding level) |  | (No corresponding level) |  | Ceiling height of at least 2.7 m in classrooms. | (No corresponding level) | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Ceiling height of at least 2.5 m in office space and windows provide all occupants with sufficient awareness of the outside environment. |  | Ceiling height at least 3.0 m in sales area. |  | Ceiling height of at least 3.0 m in classrooms. | Ceiling height at least 2.7 m in most classrooms. | ■Level 3 | Ceiling height at least 2.3 m in residential and accommodation sections.
4 | 4 |  |  | Level 4 | Ceiling height of at least 2.7 m in office space and windows provide all occupants with sufficient awareness of the outside environment. |  | Ceiling height at least 3.3 m in sales area. |  | Ceiling height of at least 3.1 m in classrooms. | (No corresponding level) | Level 4 | Ceiling height at least 2.5 m in residential and accommodation sections.
5 | 5 |  |  | Level 5 | Ceiling height of at least 2.9 m in office space and windows provide all occupants with sufficient awareness of outside the environment. |  | Ceiling height at least 3.6 m in sales area. |  | Ceiling height of at least 3.2 m in classrooms. | Ceiling height exceeding 2.7 m in classrooms. | Level 5 | Ceiling height at least 2.7 m in residential and accommodation sections.
0 | 0
|  |  |  | 1.2.2 Space for Refreshment |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Fct |  |  |  | Rtl
- | 1 |  |  | Level 1 | (No corresponding level) |  |  |  | (No corresponding level)
2 | 2 |  |  | Level 2 | There is no refreshment space. |  |  |  | Not adequate for level 3.
3 | 3 |  |  | ■Level 3 | Refreshment space is less than 1% of the working space. |  |  |  | Rest space is at least 2% of the sales floor area.
4 | 4 |  |  | Level 4 | Refreshment space is at least 1% of the working space. |  |  |  | Rest space is at least 3% of the sales floor area
5 | 5 |  |  | Level 5 | Refreshment space accounts for at least 1% of the working space and refreshment equipment such as a vending machine is provided. |  |  |  | Rest space is at least 4% of the sales floor area.
0 | 0
|  |  |  | 1.2.3 Décor Planning |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! | Residential and Accommodation Sections |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | #DIV/0! | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | #DIV/0! | Hsp,Htl,Apt
1 | 1 |  |  | #DIV/0! | Not adequate for level 3. |  |  |  | #DIV/0! | Not adequate for level 3.
- | - |  |  | #DIV/0! | (No corresponding level) |  |  |  | #DIV/0! | (No corresponding level)
3 | 3 |  |  | #DIV/0! | Applicable to two of the efforts to be evaluated. |  |  |  | #DIV/0! | Applicable to two of the efforts to be evaluated.
4 | 4 |  |  | #DIV/0! | Applicable to three of the efforts to be evaluated. |  |  |  | #DIV/0! | Applicable to three of the efforts to be evaluated.
5 | 5 |  |  | #DIV/0! | Applicable to four of the efforts to be evaluated. |  |  |  | #DIV/0! | Applicable to four of the efforts to be evaluated.
0 | 0 |  |  | Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry |  |  |  | 3 | <-- Direct entry
|  |  |  | 3 | Entire Building and Common Properties |  |  |  | 3 | Residential and Accommodation Sections
|  |  |  | Yes | The concept of the building as a whole is well defined, and specific efforts to reflect the concept are made at the décor planning stage. (For example, shifting to natural and ecological materials in a building with an ecological theme). |  |  |  |  | The concept of the building as a whole is well defined, and specific efforts to reflect the concept are made at the décor planning stage. (For example, shifting to natural and ecological materials in a building with an ecological theme).
|  |  |  | Yes | The functions required of the building have been clarified, and specific measures to encourage those functions are indicated at the décor planning stage. (For example, in Hotels and similar facilities, the interior is perceived as living space, and natural materials such as wood and stone are introduced in deliberate efforts to produce a living room-like atmosphere). |  |  |  | Yes | The functions required of the building have been clarified, and specific measures to encourage those functions are indicated at the décor planning stage. (For example, in Hotels and similar facilities, the interior is perceived as living space, and natural materials such as wood and stone are introduced in deliberate efforts to produce a living room-like atmosphere).
[5 empty] | Specific measures were taken during décor planning to integrate the lighting design (e.g. effective use of indirect lighting specific to activity type, décor planning in consideration of color temperatures of a light source, etc.). |  |  |  | Yes | Specific measures were taken during décor planning to integrate the lighting design (e.g. effective use of indirect lighting specific to activity type, décor planning in consideration of color temperatures of a light source, etc.).
[5 empty] | Mockups and interior perspectives are used to verify the décor planning in advance. |  |  |  |  | Mockups and interior perspectives are used to verify the décor planning in advance.
|  | 1.3 | Maintenance
|  |  |  | 1.3.1 Design That Considers Maintenance |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! |  | Floor area = | 0 | Note
式設定 | #DIV/0! |  |  | #DIV/0! | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Apt,Fct
|  |  |  | #DIV/0! | (No corresponding level)
|  |  |  | #DIV/0! | Building plan includes insufficient level of consideration of maintenance. (0-2 applicable measures included)
|  |  |  | #DIV/0! | Building plan includes standard level of consideration of maintenance. (3-5 applicable measures included)
|  |  |  | #DIV/0! | Building plan includes higher-than-standard level of consideration of maintenance. (6-8 applicable measures included)
|  |  |  | #DIV/0! | Building plan includes excellent level of consideration of maintenance. (9 or more applicable measures included)
新築 |  |  |  | Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry
- | 1 |  |  | 3 | Description
2 | 2 |  |  | Yes | (1) Interior finishes: Interior walls use finish methods, materials, paints or coatings that are highly dirt resistant.
3 | 3 |  |  | Yes | (2) Interior finishes: Floors use finish methods, materials, paints or coatings that are highly dirt resistant.
4 | 4 |  |  | Yes | (3) Décor planning: The design and structure of floors enables washing with water.
5 | 5 |  |  |  | (4) Décor design: Design of interior walls and floors avoids creating dust traps and places to leave objects.
0 | 0 |  |  |  | (5) Décor design: The first and second doors of windbreak lobbies are distanced so that they are not open at the same time, or are otherwise designed to prevent the entry of dust, etc.
(6) Décor design: Floor materials with very different maintenance methods are not placed close together.
(7) Exterior finishes: Exterior walls and glass are designed with highly dirt resistant construction materials, or with finishes such as weather-resistant paint and hydrophilic properties.
(8) Facade design: exterior walls are designed to maintain clean surface conditions by preventing water pooling and wet-dry effects from rain water by using rain flashing.
(9) Facade design: Measures have been applied to prevent damage from the droppings of birds (pigeons, crows, starlings, etc.).
(10) Facade design: Metal parts exposed on the exterior are plated or otherwise treated against corrosion.
|  |  |  | Yes | (11) Décor and exterior space design: Movement routes, including outdoor spaces and management areas, are designed to eliminate steps as far as possible (steps not exceeding around 5 mm).
(12) Other: Efforts have been made in areas other than the above, with consideration for maintenance.
|  |  |  | Total = | 4 | measure(s)
既存 |  |  |  | Ⅰ 建築Rtl衛生法における特定建築Rtlの場合にEfforts to be evaluated |  |  |  |  | 特定建築Rtlに該当する場合の取組みで評価する
|  |  |  | 3 | 評価項目 |  | 評価内容 |  |  |  |  | 評価ポイント
|  |  |  | 3 | 1) 業務仕様 |  | 清掃管理および設備管理仕様書の基本方針において環境配慮を明示している。 |  |  |  |  | 3
|  |  |  | 1 | 2) 契約形態 |  | 安定した品質を維持するために業務契約期間を2年以上としている。 |  |  |  |  | 1
|  |  |  | 3 | 3) 業務手順 |  | 清掃管理と設備管理における業務標準手順書を用意している。 |  |  |  |  | 3
|  |  |  | 0 | 4) インスペクション |  | 清掃および設備の維持管理状態のインスペクション記録がある。 |  |  |  |  | 2
|  |  |  | 0 | 5) 計画 |  | 外気に接するガラス,照明の清掃を含めた計画書がある。 |  |  |  |  | 1
|  |  |  | 0 | 6) 業務員への教育 |  | 年1回以上の環境等をテーマにしたトレーニングの計画と記録がある。 |  |  |  |  | 2
|  |  |  | 0 | 7) EMS |  | 管理者が外部評価による環境マネジメントシステム(EMS)の認証を得ている。 |  |  |  |  | 1
|  |  |  | 合計＝ | 7
Ⅱ 建築Rtl衛生法における特定建築Rtlに該当しない建築Rtlの場合にEfforts to be evaluated
|  |  |  | 4 | 評価項目 |  | 評価内容 |  |  |  |  | 評価ポイント
|  |  |  | 3 | 1) 頻度 |  | 施設清掃や設備点検,清掃の箇所別頻度の設定がなされている。 |  |  |  |  | 3
|  |  |  | 3 | 2) 役割 |  | 施設清掃と設備点検,清掃における各責任者,委託先が決められている。 |  |  |  |  | 3
|  |  |  | 3 | 3) 手順 |  | 施設清掃と設備点検,清掃における作業手順書やマニュアルを用意している。 |  |  |  |  | 3
|  |  |  | 0 | 4) 点検 |  | 施設清掃と設備点検,清掃の点検記録がある。 |  |  |  |  | 2
|  |  |  | 0 | 5) 実施 |  | 施設清掃や設備点検,清掃の実施記録がある。 |  |  |  |  | 1
|  |  |  | 0 | 6) 共有 |  | 施設清掃と設備点検,清掃の点検結果を共有する機Halを設けている。 |  |  |  |  | 1
|  |  |  | 合計＝ | 9
|  |  |  | 1.3.2 Securing Maintenance Functions |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! |  | Floor area = | 0 | Note
式設定 |  |  |  | #DIV/0! | Off,Sch,Rst,Rtl,Hal,Hsp,Htl,Apt,Fct
|  |  |  | #DIV/0! | (No corresponding level) | [6 empty] | Level 3 is awarded to all buildings with a total floor space of 500 m2 or less.
|  |  |  | #DIV/0! | Insufficient level of measures have been taken to ensure functionality of maintenance system. (0-8 applicable measures in place)
|  |  |  | #DIV/0! | Standard level of measures have been taken to ensure functionality of maintenance system. (4-6 applicable measures )
|  |  |  | #DIV/0! | Higher than standard level of measures have been taken to ensure functionality of maintenance system. (7-9 applicable measures)
|  |  |  | #DIV/0! | Extensive level of measures have been taken to ensure functionality of maintenance system. (10 or more applicable measures)
新築 |  |  |  | Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry
- | 1 |  |  | 3 | Specified buildings as referred to in the Law for Maintenance of Sanitation in Buildings |  |  |  |  | Buildings other than Specified buildings
2 | 2 |  |  | Yes | [1] Adequate space has been used for cleaning staff rooms, relative to the floor area. |  |  |  |  | ---
3 | 3 |  |  | Yes | [2] Adequate space has been used for cleaning equipment rooms, relative to the floor area. |  |  |  |  | [1] Storage space for cleaning materials is included in the design.
4 | 4 |  |  | Yes | [3] The cleaning equipment rooms have washing areas with drainage channels to safe drainage facilities. |  |  |  |  | [2] Sink for cleaning materials with safe drainage is installed.* Hospital buildings secure, in addition to the above, a space in which washing machines for cleaning materials are installed, depending on the number of beds.
5 | 5 |  |  | Yes | [4] Space is planned for washing and drying mops and rags, for the sake of hygiene. |  |  |  |  | [3] Areas cleaned with water (e.g. washrooms, garbage storage, kitchens) are designed with a 2% gradient.
0 | 0 |  |  |  | [5] Adequate space has been provided for sorting waste, materials for recycling, and bulky garbage items, relative to the floor area, and an easy way to move those materials outside has been planned. |  |  |  |  | [4] Adequate space for waste material storage and removal is included in the design.
[5 empty] | [6] Cleaning sinks are installed for each toilet, or for each floor. |  |  |  |  | [5] Dedicated sinks or water taps are installed.
[5 empty] | [7] Cleaning equipment for each type of floor material has been anticipated, and the layout of electrical receptacles (numbers and spacings) for use in cleaning work has been planned accordingly. |  |  |  |  | [6] Power outlets for outside/hallway cleaning are included in the design.
[5 empty] | [8] Design ensures that maintenance work can be performed safely on exterior glass and walls, air supply and vent holes, light fixtures and other fixtures in high places. |  |  |  |  | [7] Safety of maintenance activities in high places (e.g. exterior glass, vents, lighting fixtures) is addressed in the design.
[5 empty] | [9] Suitable levels of lighting for cleaning purposes can be set. |  |  |  |  | [8] Water traps under all sinks in washrooms, hot water rooms, and kitchens can be removed for cleaning.
[5 empty] | [10] Valves and other devices requiring day-to-day adjustment are installed in positions which allow convenient operation. |  |  |  |  | [9] Devices requiring day-to-day adjustment (e.g. valves) are installed in positions which allow convenient operation.
[5 empty] | [11] Inspection access holes for equipment concealed in ceiling voids are at least 600 x 600 mm. |  |  |  |  | [10] Inspection access holes for equipment concealed in ceiling voids are at least 600 x 600 mm.
[5 empty] | [12] Equipment that is not in private areas can be accessed from common areas for maintenance. |  |  |  |  | [11] Equipment that is not in private areas can be accessed from common areas for maintenance.
[5 empty] | [13] Other than the above, points related to securing maintenance functions have been identified and implemented. |  |  |  |  | [12] Other than the above, points related to securing maintenance functions have been identified and implemented.
|  |  |  | Total = | 4 | measure(s)
Sch校版 |  |  |  | Efforts to be evaluated
|  |  |  | （１） | 大掃除の実施 |  | 大掃除は、定期に行われていること。（毎Sch年３回）
|  |  |  | （２） | 雨水の排水溝等 |  | 屋上等の雨水排水溝に、泥や砂等が堆積していないこと。また、雨水配水管の末端は、砂や泥等により管径が縮小していないこと。（毎Sch年１回）
|  |  |  | （３） | 排水の施設,設備 |  | 汚水槽、雑排水槽等の施設,設備は、故障等がなく適切に機能していること。 （毎Sch年１回）
既存 |  |  |  | Ⅰ 建築Rtl衛生法における特定建築Rtlの場合にEfforts to be evaluated |  |  | 特定建築Rtlに該当する場合の取組みで評価する |  |  | Ⅱ 建築Rtl衛生法における特定建築Rtlに該当しない建築Rtlの場合にEfforts to be evaluated
|  |  |  | 3 | 評価項目 | 評価内容 |  |  | 評価ポイント | 評価内容 |  |  | 評価ポイント
|  |  |  | 1 | 1) 汚染源対策 | 充分な長さのエントランスマットを設置している。(外部、内部含む5ｍ以上) |  |  | 1 | ある程度の長さのエントランスマットを設置している。 |  |  | 1
|  |  |  | 3 | 2) 清掃方法 | ① 清掃業務において効果的な方法を採用している。 |  |  | 3 | - |  |  | -
|  |  |  | 0 |  | ② 清掃業務において環境影響の少ない方法を採用している。 |  |  | 3 | - |  |  | -
|  |  |  | 2 |  | - |  |  | - | ① トイレ、共用部、厨房、玄関マットは毎日、清掃を実施するOffとしている。 |  |  | 2
|  |  |  | 0 |  | - |  |  | - | ② 希釈をする洗浄剤の希釈方法を明記している。 |  |  | 1
|  |  |  | 0 | 3) 清掃資材 | ① 環境ラベル取得製品の採用。(エコマーク、グリーンマークなど) |  |  | 1 | ① 環境ラベル取得製品を採用している。（エコマーク、グリーンマークなど） |  |  | 1
|  |  |  | 0 |  | ② 清掃用ケミカルのⅰ 床用保護剤、ⅱ 床用洗浄剤(カーペット含む)、ⅲ トイレ用洗浄剤、ⅳ ガラス用洗浄剤の4製品に関して、環境負荷と安全に配慮した製品を採用している。(判定表を参照) |  |  | 2 | ② 清掃資材専用の保管スペースがある。 |  |  | 2
|  |  |  | 1 |  | - |  |  | 1 | ③ トイレ、共用部、厨房などの清掃に使用するケミカルの2種類以上についてMSDS（化SchRtl質安全データシート）を保管している。 |  |  | 1
|  |  |  | 0 | 4) 感染症対策 | 清掃業務において感染症対策に配慮した方法を採用している。 |  |  | 1 | ① トイレ清掃では除菌剤配合洗剤を使用している。 |  |  | 1
|  |  |  | 0 |  | - |  |  | 1 | ② 感染防止を考慮した嘔吐Rtlの処理方法がある。 |  |  | 1
|  |  |  | 0 | 5) 安全対策 | 清掃業務において安全に配慮した方法を採用している。 |  |  | 2 | 手袋、メガネ、マスクなどの保護具の着用を促している。 |  |  | 2
|  |  |  | 合計＝ | 4
判定表
|  |  |  | 評価項目 |  | 判定基準
|  |  |  | 水素イオン濃度（pH） |  | 原液＝pH5～pH9であるOff。
|  |  |  | シックハウス配慮 |  | ⅰ 床用保護剤 |  | 厚生労働省策定の「室内濃度に関する指針値」対象Rtl質である揮発性有機化合Rtl(VOC)を原料に含まないOff。原料に含まれる場合は、JIS K 3920（フロアーポリッシュ試験方法）-24（皮膜からの放散成分分析）を実施し、その分析値が室内濃度指針値以下であるOff。
[6 empty] | ⅱ 床用洗浄剤 ⅲ トイレ用洗浄剤 ⅳ ガラス用洗浄剤 |  | 厚生労働省策定の「室内濃度に関する指針値」対象Rtl質である揮発性有機化合Rtl(VOC)を原料に含まないOff。
|  |  |  | 急性経口毒性 |  | LD50：＞2,000mg/kgであるOff。
|  |  |  | VOC濃度 |  | 製品が定める最も高濃度希釈時のVOC含有率が洗浄剤＜1% 床用保護剤＜7%であるOff。（沸点260℃未満のVOC対象）
|  |  |  | 有害性が判明している化SchRtl質 |  | 特定化SchRtl質の環境への排出量の把握等及び管理の改善の促進に関する法律（ＰＲＴＲ法）の「第一種指定化SchRtl質」と「第二種指定化SchRtl質」が指定割合以下であるOff。
既存 |  |  |  | 1.3.3 衛生管理業務 |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  | 延床面積＝ | 0
|  |  |  | #DIV/0! | Off,Sch,Rtl,Hal,Htl | [6 empty] | 備考
|  |  |  | #DIV/0! | (該当するレベルなし) | [6 empty] | 延床面積500㎡以下の建築Rtlは レベル3とする。 注）500㎡以下の建Rtlは直接入力により、レベル3を選択してください。
|  |  |  | #DIV/0! | 3つの設備管理業務の取り組みポイントで-１(ﾚﾍﾞﾙ2)の取り組みがひとつでもある場合
|  |  |  | #DIV/0! | 3つの設備管理業務の取り組みポイントが 0点
|  |  |  | #DIV/0! | 3つの設備管理業務の取り組みポイントが 1～2点
|  |  |  | #DIV/0! | 3つの設備管理業務の取り組みポイントが 3点
Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry
1 | 1 |  |  | 3 | 評価項目 |  | 建築Rtl衛生法における特定建築Rtl |  |  | 建築Rtl衛生法における特定建築Rtlに該当しない建築Rtl |  |  | ポイント
2 | 2 |  |  | 0 | Ⅰ 空調管理の評価 |  | 建築Rtl環境衛生管理基準の空調設備において不適切項目がある。 |  |  | 空調管理は何も実施していない。 |  |  | -1（レベル2）
3 | 3 |  |  | 0 |  |  | 建築Rtl環境衛生管理基準を満たし、フィルターの定期的な点検,清掃を行っている。 |  |  | 建築基準法施行細則第8条（建築設備等の定期報告）に基づく換気設備定期点検を年1回実施し、改善している。 ※特定行政庁が規定する特殊建築Rtlに該当しない場合は取組み「0点」として評価する。 |  |  | 0
4 | 4 | [5 empty] | 建築Rtl環境衛生管理基準を満たした以上に、特別な対策を行っている。 |  |  | 建築Rtl環境衛生管理基準レベルの空調管理を実施し、記録を保管している。 |  |  | 1
5 | 5 |  |  | 0 | Ⅱ ねずみ等の点検,防除の評価 |  | 建築Rtl環境衛生管理基準の害虫駆除において不適切項目がある。 |  |  | ねずみ等の点検,防除は何も実施していない。 |  |  | -1（レベル2）
0 | 0 |  |  | 0 |  |  | 建築Rtl環境衛生管理基準を満たし、6ヶ月に1回の点検および防除を行っている。 |  |  | 各建築Rtlに適用されている法律、規則、基準などに則り、ねずみ等の点検,防除を定期的に実施している。 ※法律、規則、基準などがない建築Rtlの場合は年1回のねずみ等の点検,防除を実施している。 |  |  | 0
[7 empty] | 建築Rtl環境衛生管理基準を満たした以上に、特別な対策を行っている。 |  |  | 建築Rtl環境衛生管理基準レベルのねずみ等の点検,防除を実施し、記録を保管している。 |  |  | 1
|  |  |  | 0 | Ⅲ 給水,給湯管理 （Rst用,炊Off用,浴用等）の評価 |  | 建築Rtl環境衛生管理基準の給水設備において不適切項目がある。 |  |  | 給水,給湯管理（Rst用,炊Off用,浴用等）は何も実施していない。 |  |  | -1（レベル2）
|  |  |  | 0 |  |  | 建築Rtl環境衛生管理基準を満たしている。 |  |  | 「水道法」に基づき、受水槽の清掃や水質の外部検査を年1回実施し、改善している。 ※直結式給水で受水槽がない場合は取組み「0点」として評価する。 |  |  | 0
[7 empty] | 建築Rtl環境衛生管理基準を満たした以上に、特別な対策を行っている。 |  |  | 建築Rtl環境衛生管理基準レベルの給水,給湯管理（Rst用,炊Off用,浴用等）を実施し、記録を保管している。 |  |  | 1
|  |  |  | 合計＝ | 0
|  | 2 | Durability & Reliability
|  | 2.1 | Earthquake Resistance
|  |  |  | 2.1.1 Earthquake-resistance |  |  |  | #DIV/0! | 2.1.2 Seismic Isolation & Vibration Damping Systems |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch(Univ.,etc),Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  | Sch（ES/JS/JHS） |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | - |  |  | Level 1 | (No corresponding level) |  | (No corresponding level) |  | Level 1 | (No corresponding level)
2 | - |  |  | Level 2 | (No corresponding level) |  | The building's earthquake resistance meets the requirements of the Building Standard Law. |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | The building's earthquake resistance meets the requirements of the Building Standard Law. |  | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 25% margin. |  | ■Level 3 | No seismic isolation or vibration damping system is used.
4 | 4 |  |  | Level 4 | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 25% margin. |  | (No corresponding level) |  | Level 4 | A vibration damping system is installed. Improved comfort in strong wind is considered.
5 | 5 |  |  | Level 5 | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 50% margin. Alternatively, damage control design has been used. |  | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 50% margin. Alternatively, damage control design has been used. |  | Level 5 | A seismic isolation system is used.
0 | 0
|  | 2.2 | Service Life of Components
|  |  |  | 2.2.1 Service Life of Structural Materials |  |  |  | #DIV/0! | 2.2.2 Necessary Refurbishment Interval for Exterior Finishes |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | Less than 10 years
- | 2 |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | 10 years or more, less than 20 years
3 | 3 |  |  | ■Level 3 | Level equivalent to Grade 1 in the assessment standards for wood, steel frame and concrete structures (MLIT directive 151 issued in 2014, regarding Section 3. Reduction of Deterioration in the Japan Housing Performance Standards, under the Housing Quality Assurance Act) |  |  |  | ■Level 3 | 20 years
4 | 4 |  |  | Level 4 | Level equivalent to Grade 2 in the assessment standards for wood, steel frame and concrete structures (MLIT directive 151 issued in 2014, regarding Section 3. Reduction of Deterioration in the Japan Housing Performance Standards, under the Housing Quality Assurance Act) |  |  |  | Level 4 | 21 years or more, less than 30 years
5 | 5 |  |  | Level 5 | Level equivalent to Grade 3 in the assessment standards for wood, steel frame and concrete structures (MLIT directive 151 issued in 2014, regarding Section 3. Reduction of Deterioration in the Japan Housing Performance Standards, under the Housing Quality Assurance Act) |  |  |  | Level 5 | 30 years or more
0 | 0
|  |  |  | 2.2.3 Necessary Renewal Interval for Main Interior Finishes |  |  |  | #DIV/0! | 2.2.4 Necessary Replacement Interval for Air Conditioning and Ventilation Ducts |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  | Apt |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | - |  |  | Level 1 | Less than 5 years |  | Less than 10 years |  | Level 1 | (No corresponding level)
2 | - |  |  | Level 2 | 5 years or more, less than 10 years |  | 10 years or more, less than 15 years |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | 10 years |  | 15 years |  | ■Level 3 | Zinc-plated steel sheet used almost throughout.
4 | 4 |  |  | Level 4 | 11 years or more, less than 20 years |  | 16 years or more, less than 25 years |  | Level 4 | Exposed exterior ducts, kitchen venting ducts, high-humidity venting ducts and similar applications that would have shorter service lives than other applications when made from zinc-plated steel sheet are made from stainless steel or Galvalume to extend service life. Alternatively, appropriate provision has been made for drainage of internal condensation.
5 | 5 |  |  | Level 5 | 20 year or more |  | 25 years or more |  | Level 5 | At least 90% of exposed exterior ducts, kitchen venting ducts, high-humidity venting ducts and similar applications that would have shorter service lives than other applications when made from zinc-plated steel sheet are made from stainless steel or Galvalume to extend service life.
0 | 0
|  |  |  | 2.2.5 Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes |  |  |  | #DIV/0! | 2.2.6 Necessary Renewal Interval for Major Equipment and Services |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | Less than 7 years
- | 2 |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | 7 years or more, less than 15 years
3 | 3 |  |  | ■Level 3 | D or better used in almost all the top three main building types. |  |  |  | ■Level 3 | 15 years
4 | 4 |  |  | Level 4 | C or better used in at least two of the top three main building types. |  |  |  | Level 4 | 16 years or more, less than 30 years
5 | 5 |  |  | Level 5 | B or better used in at least two of the top three main building types, and E is not used. |  |  |  | Level 5 | 30 years or more
0 | 0
|  | 2.3 | Appropriate Renewal |  |  | <N.A.>
既存で評価 |  |  |  | 2.3.1 屋上（屋根）,外壁仕上げ材の更新 |  |  |  | #DIV/0! | 2.3.2 配管,配線材の更新 |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | メンテナンス記録がなく判定不可能。 |  |  |  | Level 1 | メンテナンス記録がなく判定不可能。
2 | 2 |  |  | Level 2 | 全て耐用年数を超えている。 |  |  |  | Level 2 | 全て耐用年数を超えている。
3 | 3 |  |  | ■Level 3 | 主要機器は耐用年数以内である。 |  |  |  | ■Level 3 | 主要機器は耐用年数以内である。
- | - |  |  | Level 4 | (該当するレベルなし) |  |  |  | Level 4 | (該当するレベルなし)
5 | 5 |  |  | Level 5 | 全て耐用年数以内である。 |  |  |  | Level 5 | 全て耐用年数以内である。
0 | 0
既存で評価 |  |  |  | 2.3.3 主要設備機器の更新 |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | メンテナンス記録がなく判定不可能。
2 | 2 |  |  | Level 2 | 全て耐用年数を超えている。
3 | 3 |  |  | ■Level 3 | 主要機器は耐用年数以内である。
- | 4 |  |  | Level 4 | (該当するレベルなし)
5 | 5 |  |  | Level 5 | 全て耐用年数以内である。
0 | 0
|  | 2.4 | Reliability
2.4.1 HVAC System
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | #DIV/0! | Off,Hal,Hsp,Htl,Fct |  | Sch,Rtl,Rst,Apt |  | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt [<2000m2]
|  |  |  | #DIV/0! | No efforts to be evaluated. |  | No efforts to be evaluated. |  | (No corresponding level)
|  |  |  | #DIV/0! | (No corresponding level) |  | (No corresponding level) |  | (No corresponding level)
|  |  |  | #DIV/0! | Applicable to one of the efforts to be evaluated. Alternatively, there is no centralized HVAC system. |  | Applicable to one of the efforts to be evaluated. Alternatively, there is no centralized HVAC system. |  | No applicable measure is established
|  |  |  | #DIV/0! | Applicable to two of the efforts to be evaluated. |  | (No corresponding level) |  | One applicable measure is established
|  |  |  | #DIV/0! | Applicable to three or more of the efforts to be evaluated. |  | Applicable to two or more of the efforts to be evaluated. |  | Two or more applicable measures are established
Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry
1 | 1 |  |  | Building type | Off,Hal,Hsp,Htl,Fct |  | Sch,Rtl,Rst,Apt |  | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt [<2000m2]
- | 2 |  |  | Floor area | 0 | m2 | 0 | m2 | 0 | m2
3 | 3 |  |  | Score | 3 |  | 3 |  | 4
4 | 4 |  |  | Yes | 1) Circuits are divided according to the importance of their ventilation equipment, and more important circuits are given priority in operation after a disaster. Also, ways of running the ventilation with reduced load capacity have been examined.
5 | 5 |  |  |  | 2) Dispersion and duplication of heat source types (electricity, gas, etc.), with backups.
0 | 0 |  |  |  | 3) Countermeasures (such as suspended pipes) have been taken to ensure that overall function can continue even when the building is partially damaged by an earthquake.
4) Circuits are divided according to the importance of their air conditioning equipment, and more important circuits are given priority in operation after a disaster. Also, ways of running the air conditioning with reduced load capacity have been examined.
2.4.2 Water Supply & Drainage
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | #DIV/0! | Off,Sch,Hal,Hsp,Htl,Fct,Apt |  |  | Rtl,Rst
|  |  |  | #DIV/0! | No efforts to be evaluated. |  |  | No efforts to be evaluated.
|  |  |  | #DIV/0! | Applicable to one of the efforts to be evaluated. |  |  | Applicable to one of the efforts to be evaluated.
|  |  |  | #DIV/0! | Applicable to two of the efforts to be evaluated. |  |  | Applicable to two of the efforts to be evaluated.
|  |  |  | #DIV/0! | Applicable to three of the efforts to be evaluated. |  |  | (No corresponding level)
|  |  |  | #DIV/0! | Applicable to four or more of the efforts to be evaluated. |  |  | Applicable to three or more of the efforts to be evaluated.
Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry
1 | 1 |  |  | Building type | Off,Sch,Hal,Hsp,Htl,Fct,Apt |  |  | Rtl,Rst
- | 2 |  |  | Floor area | 0 | m2 |  | 0 | m2
3 | 3 |  |  | Score | 3 |  |  | 3
4 | 4 |  |  | Yes | Water-saving equipment is used. This is limited to cases where it is used on a majority of the installed equipment. Water-saving devices are those approved as Eco Mark products, or those equivalent to water-saving equipment that is the approval standard for Eco Mark products (Toilet bowls: approx. 6 L/use, urinals: approx. 4 L/use).
5 | 5 |  |  |  | Plumbing systems are separated as far as possible to reduce the portions that become unserviceable in the event of a disaster.
0 | 0 |  |  |  | The building has a pit for temporary waste water storage, in case mains sewerage is unavailable after a disaster.
|  |  |  | Yes | The building has two separate tanks, one for water reception and one elevated tank.
Planning enables the use of well water, gray water, etc.
The building is equipped with a simple filtration system allowing conversion of rain water to potable water in the event of a disaster (Not applied to Rtl and Rst).
A faucet is provided in the water tank so that the water may be used for drinking in case of a power outage due to a disaster.
|  |  |  | Total = | 2 | measure(s) |  | 2 | measure(s)
2.4.3 Electrical Equipment
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt [<2000m2]
|  |  |  | Level 1 | No efforts to be evaluated. |  |  |  | (No corresponding level)
|  |  |  | Level 2 | (No corresponding level) |  |  |  | (No corresponding level)
|  |  |  | ■Level 3 | Applicable to one or more of the efforts to be evaluated. |  |  |  | No efforts to be evaluated.
|  |  |  | Level 4 | Applicable to three of the efforts to be evaluated. |  |  |  | Applicable to one of the efforts to be evaluated.
|  |  |  | Level 5 | Applicable to four or more of the efforts to be evaluated. |  |  |  | Applicable to two or more of the efforts to be evaluated.
Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry
1 | 1 |  |  | Building type | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt [<2000m2]
3 | 3 |  |  | Score | 3 |  |  |  | 3
4 | 4 |  |  |  | 1) Emergency generator is installed.
5 | 5 |  |  |  | 2) Uninterruptible power supply system is installed
0 | 0 |  |  |  | 3) Redundant power receiving system for key service equipment is installed.
|  |  |  | Yes | 4) Measures described in Item A and B below have been established in order to avoid power outages or damage to data network caused by flooding in power supply equipment or precision machinery (in apartments, circuit breakers, distribution boards, etc.), or Item C applies. A. Power supply equipment and precision machinery are not installed below ground level. B. Water blocking devices (e.g. waterproof doors and panels, raised mounds, dry ditches) and drainage system (e.g. pumps, etc.) are installed to prevent flooding below ground level. C. No danger of flooding. (Not applicable to buildings with a total floor space of less than 2,000 m2)
5) Wiring is installed for lighting and other equipment available when connected to a power-supply car.
6) Power supply is secured from two different substations.
|  |  |  | 2.4.4 Support Method of Machines & Ducts |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Not adequate for level 3.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Earthquake resistance class†1 B (Human safety is assured and secondary damage prevented after a major earthquake). Or, the design lateral seismic coefficient KH is more than 1.0 after conducting the dynamic analysis.
4 | 4 |  |  | Level 4 | Earthquake resistance class A (In addition to Class B, important functions can be secured without major repairs). Or, the design lateral seismic coefficient KH is more than 1.5 after conducting the dynamic analysis.
5 | 5 |  |  | Level 5 | Earthquake resistance class S (In addition to Class A, all functions can be secured without major repairs). Or, the design lateral seismic coefficient KH is more than 2.0 after conducting the dynamic analysis.
0 | 0
2.4.5 Communications & IT Equipment
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | No efforts to be evaluated.
|  |  |  | Level 2 | Applicable to one of the efforts to be evaluated.
|  |  |  | ■Level 3 | Applicable to two of the efforts to be evaluated.
|  |  |  | Level 4 | Applicable to three of the efforts to be evaluated.
|  |  |  | Level 5 | Applicable to four of the efforts to be evaluated.
Efforts to be evaluated
|  |  |  | 3 | <-- Direct entry
1 | 1 |  |  | Building type | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
4 | 4 |  |  |  | 1) Communications methods are diversified, using optical fiber cable, metal cable, cellular telephone network, PHS network and others.
5 | 5 |  |  |  | 2) Connections are made from two telephone exchanges to secure two communications links.
|  |  |  | Yes | 3) Countermeasures Item A and B below have been taken or Item C applies, in order to avoid damage to data networks due to water percolation into precision machinery. A. Installation of precision machinery below ground is avoided. B. Devices to prevent the groundwater percolation (waterproof doors, waterproof panels, embankments, dry ditches) and drainage equipment (pumps, etc.) are installed. C. No danger of water percolation.
4) Wire telephones, FAX and community emergency radio systems are installed in case of a disaster.
|  |  |  | Yes | 5) Disaster information is available through a cable TV or other channels in the event of a disaster.
0 | 0 |  |  |  | 6) An uninterruptible power supply system is installed for network devices.
|  | 3 | Flexibility & Adaptability
|  | 3.1 | Spatial Margin
|  |  |  | 3.1.1 Allowance for Floor-to-floor Height |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! | Residential and Accommodation Sections |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hsp,Fct |  | Off,Sch,Rtl,Rst,Hsp,Fct [<2000m2] |  | 3 | Hsp,Htl |  | Apt
1 | 1 |  |  | Level 1 | Less than 3.3 m |  | Less than 3.1 m |  | Level 1 | Less than 3.3 m |  | Less than 2.7 m
2 | 2 |  |  | Level 2 | 3.3 m or more, less than 3.5 m |  | 3.1 m or more, less than 3.3 m |  | Level 2 | 3.3 m or more, less than 3.5 m |  | 2.7 m or more, less than 2.8 m
3 | 3 |  |  | ■Level 3 | 3.5 m or more, less than 3.7 m |  | 3.3 m or more, less than 3.5 m |  | ■Level 3 | 3.5 m or more, less than 3.7 m |  | 2.8 m or more, less than 2.9 m
4 | 4 |  |  | Level 4 | 3.7 m or more, less than 3.9 m |  | 3.5 m or more, less than 3.7 m |  | Level 4 | 3.7 m or more, less than 3.9 m |  | 2.9 m or more, less than 3.0 m
5 | 5 |  |  | Level 5 | 3.9 m or more |  | 3.7 m or more |  | Level 5 | 3.9 m or more |  | 3.0 m or more
0 | 0
|  |  |  | 3.1.2 Flexibility in Floor Layout |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! | Residential and Accommodation Sections |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Fct |  |  |  | 3 | Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 0.7 ≦ [Wall length/area ratio] |  |  |  | Level 1 | 0.7 ≦ [Wall length/area ratio]
2 | 2 |  |  | Level 2 | 0.5 ≦ [Wall length/area ratio] < 0.7 |  |  |  | Level 2 | 0.5 ≦ [Wall length/area ratio] < 0.7
3 | 3 |  |  | ■Level 3 | 0.3 ≦ [Wall length/area ratio] < 0.5 |  |  |  | ■Level 3 | 0.3 ≦ [Wall length/area ratio] < 0.5
4 | 4 |  |  | Level 4 | 0.1 ≦ [Wall length/area ratio] < 0.3 |  |  |  | Level 4 | 0.1 ≦ [Wall length/area ratio] < 0.3
5 | 5 |  |  | Level 5 | [Wall length/area ratio] < 0.1 |  |  |  | Level 5 | [Wall length/area ratio] < 0.1
0 | 0 |  |  |  | Wall length/area ratio = | Length of perimeter walls (m) + length of bearing walls (m)
Exclusive area (m2)
|  | 3.2 | Floor Load Margin |  |  |  |  | #DIV/0!
|  |  |  | Entire Building and Common Properties |  |  | Weighting coefficients(default) = | #DIV/0! |  |  | Residential and Accommodation Sections | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Rtl,Rst,Hal(fixed sheets),Hsp,Fct |  | Hal(unfixed sheets) |  | Sch |  | 3 | Hsp,Htl,Apt
- | - |  |  | Level 1 | (No corresponding level) |  | (No corresponding level) |  | (No corresponding level) |  | Level 1 | (No corresponding level)
2 | 2 |  |  | Level 2 | Less than 2,900 N/m2 |  | Less than 3,500 N/m2 |  | Less than 2,300 N/m2 |  | Level 2 | Less than 1,800 N/m2
3 | 3 |  |  | ■Level 3 | 2,900 N/m2 or more, less than 3,500 N/m2 |  | 3,500 N/m2 or more, less than 4,200 N/m2 |  | 2,300 N/m2 or more, less than 2,900 N/m2 |  | ■Level 3 | 1,800 N/m2 or more, less than 2,100 N/m2
4 | 4 |  |  | Level 4 | 3,500 N/m2 or more, less than 4,500 N/m2 |  | 4,200 N/m2 or more, less than 5,200 N/m2 |  | 2,900 N/m2 or more, less than 3,500 N/m2 |  | Level 4 | 2,100 N/m2 or more, less than 2,900 N/m2
5 | 5 |  |  | Level 5 | 4,500 N/m2 or more |  | 5,200 N/m2 or more |  | 3,500 N/m2 or more |  | Level 5 | 2,900 N/m2 or more
0 | 0
|  | 3.3 | System Renewability
|  |  |  | 3.3.1 Ease of Air Conditioning Duct Renewal |  |  |  |  | 3.3.2 Ease of Water Supply and Drain Pipe Renewal
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Air conditioning ducts cannot be replaced or repaired without damaging structural elements. |  |  |  | Level 1 | Repair and replacement are not possible without damaging structural elements and finishes.
2 | 2 |  |  | Level 2 | In some cases the air conditioning ducts can be replaced or repaired without damaging structural elements, if spare sleeves are used, but that method cannot be applied to all ducts. |  |  |  | Level 2 | Repairs can be made without damaging structural elements, but replacements cannot.
3 | 3 |  |  | ■Level 3 | Space and routes for future use (future replacement work) have been provided, so that nearly all air conditioning ducts can be replaced or repaired without damaging structural elements. Alternatively, there is no central air conditioning equipment. |  |  |  | ■Level 3 | Repairs can be made without damaging structural elements and finishes, but replacements cannot.
4 | 4 |  |  | Level 4 | Exterior air conditioning ducts are used or ceiling space provided so that ducts can be replaced or repaired without damaging either structural elements or surface finishes. |  |  |  | Level 4 | Repairs and replacements can be made without damaging structural elements.
5 | 5 |  |  | Level 5 | ISS*, equipment floor installation or other measures allow easy replacement or repair of air conditioning ducts without damaging surface finishes. |  |  |  | Level 5 | Repair and replacement are possible without damaging structural elements or finishes.
0 | 0
|  |  |  | 3.3.3 Ease of Electrical Wiring Renewal |  |  |  |  | 3.3.4 Ease of Communications Cable Renewal
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Wiring cannot be replaced or repaired without damaging structural elements. |  |  |  | Level 1 | Communications cables cannot be replaced or repaired without damaging structural elements.
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Wiring can be replaced or repaired without damaging structural elements. |  |  |  | ■Level 3 | Communications cables can be replaced or repaired without damaging structural elements.
- | - |  |  | Level 4 | (No corresponding level) |  |  |  | Level 4 | (No corresponding level)
5 | 5 |  |  | Level 5 | Wiring can be replaced or repaired without damaging structural elements or surface finishes. |  |  |  | Level 5 | Communications cables can be replaced or repaired without damaging structural elements or surface finishes.
0 | 0
|  |  |  | 3.3.5 Ease of Equipment Renewal |  |  |  |  | 3.3.6 Provision of Backup Space
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | - |  |  | Level 1 | No machine hatches or routes to accommodate replacement of major service equipment are provided, and building functions cannot be maintained through replacement and repair. |  |  |  | Level 1 | (No corresponding level)
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Machine hatches or routes to accommodate replacement of major service equipment are provided, but building functions cannot be maintained through replacement and repair. |  |  |  | ■Level 3 | There is no planned provision of space for backup equipment.
4 | 4 |  |  | Level 4 | A temporary space to accommodate replacement of major service equipment is secured, and building functions can be maintained through replacement and repair. |  |  |  | Level 4 | There is planned provision of space for backup equipment.
5 | - |  |  | Level 5 | Machine hatches or routes to accommodate replacement of major service equipment are provided, and building functions can be maintained through replacement and repair. |  |  |  | Level 5 | (No corresponding level)
0 | 0
Note on H123: 500㎡未満の建物は直接入力により、レベル３を選択してください。
Note on H176: レベル３は、直接入力より選択。 500㎡未満の建物は直接入力により、レベル３を選択してください。

## Q3
[8 empty] | ■Building Name | XXX Building |  | プルダウン選択肢
|  | Q3 Outdoor Environment (On-site) |  |  |  |  | Select from pull-down menus or enter figures and comments. |  |  |  | 0 | Yes |  | Preliminary design stage
[11 empty] | 1 |  | ON | Execution design stage
|  | 1 | Preservation & Creation of Biotope | [7 empty] | 2 |  |  | Construction completion stage
[8 empty] | Weighting coefficients(default) = |  | #DIV/0! |  | はい
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [5 empty] | - | いいえ
|  |  |  | Level 1 | No consideration has been given to the conservation and creation of habitat, and efforts are inadequate.(0-3 points)
|  |  |  | Level 2 | Some consideration has been given to the conservation and creation of habitat, but efforts are still somewhat inadequate.(4-6 points)
|  |  |  | ■Level 3 | Consideration has been given to the conservation and creation of habitat, and a standard level of efforts are being carried out.(7-9 points) | [6 empty] | 1 | Level 1 | ■Level 1
|  |  |  | Level 4 | Consideration has been given to the conservation and creation of habitat, and a relatively high level of efforts are being carried out. (10-12 points) | [6 empty] | 2 | Level 2 | ■Level 2
|  |  |  | Level 5 | Thorough consideration has been given to the conservation and creation of habitat, and a high level of efforts have been carried out. (13 or more points) | [6 empty] | 3 | Level 3 | ■Level 3
[5 empty] | Efforts to be evaluated | [6 empty] | 4 | Level 4 | ■Level 4
[5 empty] | point(s) | Assessment Item | Description |  |  | allocated point(s) |  | 5 | Level 5 | ■Level 5
既存はなし |  |  |  |  | 2 | I. Identification of local characteristics and biotope plan policy | 1) Local characteristics of the site and surrounding areas regarding habitat are identified and an appropriate biotope plan policy has been established |  |  | 2 |  | 0 | レベル | レベル
[5 empty] | 2 | II. Conservation and restoration of biological resources | 1) Biological resources on site are protected or restored (e.g. flora and fauna, topsoil, wetland area composition) |  |  | 2
[5 empty] | 1 | lll. Use of Green Space | 1) Green areas account for 10% or more but less than 20% of the total outside property area and mid/high trees are planted. (1 point) |  |  | 1～3
- Green areas account for 20% or more but less than 50% of the total outside property area. (2 points)
- Green areas account for 50% or more of the total outside property area. (3 points)
[5 empty] | 1 |  | 2) Building greenery index is measured at 0.05 or higher but less than 0.2. (1 point) |  |  | 1～2
- Building greenery index is measured at 0.2 or higher. (2 points)
[5 empty] | 1 | IV. Quality of Green Space | 1) The greenery plan facilitates conservation of native/local species. |  |  | 1
[5 empty] | 0 |  | 2) The greenery plan is appropriate for site and building characteristics. |  |  | 1
[5 empty] | 0 |  | 3) The greenery plan facilitates conservation of natural areas inhabited by small animals. |  |  | 1
[5 empty] | 0 | V. Management and use of biological resources | 1) Equipment necessary for the maintenance of green areas at the building operation stage have been installed, and management policies have been established. |  |  | 1
[5 empty] | 0 |  | 2) An environment and facilities have been provided in which building users and local people can encounter living creatures and enjoy nature. |  |  | 1
[5 empty] | 0 | VI. Other | 1) Independent efforts other than the above evaluated items have been implemented to protect and create habitat. |  |  | 1
[5 empty] | Total = | 7
|  | 2 | Townscape & Landscape
[8 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | (0 points)
|  |  |  | Level 2 | Sufficient level of measures for the surrounding landscape have not established. (1-2 points)
|  |  |  | ■Level 3 | Sufficient level of measures for the surrounding landscape have been established. (3 points)
|  |  |  | Level 4 | More than the sufficient level of measures for the surrounding landscape have been established. (4 points)
|  |  |  | Level 5 | Extensive level of measures for the surrounding landscape have been established. (or the building has won local landscape-related awards; 5 or more points)
[5 empty] | 3 | <-- Direct entry
[1] Evaluate level three if the building is almost entirely unseen from public spaces, or if there is no way to give consideration to urban context and scenery. [2] Evaluate efforts based on the locally applied rules, such as urban context guidelines, etc., if any. [3] Evaluate level five if scenery is clearly stated as a reason for winning a local scenery prize, or any similar situation indicating the building has gained a certain level of positive assessment.
Efforts to be evaluated
[5 empty] | point(s) | Assessment Item | Description |  |  | allocated point(s)
[5 empty] | 2 | 1) Integration with surrounding landscape through positioning and design of the building | Building features are designed in harmony with surrounding landscape (i.e. height, wall positions, color and form of exterior finish, roof, eaves, openings fences, etc.). |  |  | 2
[5 empty] | 1 | 2) Use of green space to enhance landscape | Aesthetic landscape is created by the building's green space. |  |  | 1
[5 empty] | 0 | 3) Conservation of historic landscape | Historic landscape is maintained through conservation, restoration or recreation of the exterior of historic buildings and the existing natural environment the area. |  |  | 1
[5 empty] | 0 | 4) Use of local materials to enhance landscape | Locally-significant materials are used in the building exterior to create aesthetic landscape. |  |  | 1
[5 empty] | 0 | 5) Aesthetics from main viewpoints of surrounding area | Aesthetic panoramic view of the building and surrounding areas is offered from nearby parks and gathering space or distant viewpoints. |  |  | 1
[5 empty] | 0 | 6) Other | Other (state content) |  |  | 1
[5 empty] | Total = | 3
|  | 3 | Local Characteristics & Outdoor Amenity
|  | 3.1 | Attention to Local Character & Improvement of Comfort
既存 | [7 empty] | Weighting coefficients(default) = |  | #DIV/0!
式修正 | → |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | No efforts have been made for local characteristics and outdoor amenity. (0 points)
|  |  |  | Level 2 | Efforts based on local characteristics and outdoor amenity are inadequate. (1 point)
|  |  |  | ■Level 3 | Efforts based on local characteristics and outdoor amenity are at a standard level. (2-3 points)
|  |  |  | Level 4 | Efforts based on local characteristics and outdoor amenity are at a relatively high level. (4 points)
|  |  |  | Level 5 | Efforts based on local characteristics and outdoor amenity are thorough and extensive. (5 or more points)
Efforts to be evaluated
[5 empty] | point(s) | Assessment Item | Description |  |  | allocated point(s)
[5 empty] | 1 | I. Continuation of unique local character, history and culture | 1) Conservation of historic built spaces etc. Historic interior and exterior spaces building remains preserved, restored or regenerated, contributing to local culture. (Do not evaluate if measures here overlap with areas evaluated under urban context and scenery.) |  |  | 1
[5 empty] | 1 |  | 2) Use of locally-significant materials Local materials are partially used in the building's structure, interior finishes or exterior space. (Do not include measures evaluated under the local landscape section.) |  |  | 1
[5 empty] | 1 | II. Local contribution through provision of functional spaces and facilities | 1) Local contribution by provision of space |  |  | 1
Structural measures such as provision of alcoves, piloti and eaves are used to provide amenity for people using urban spaces, in the form of places to shelter from rain or wait for people.
Or, space is provided in plazas, paths and side streets to provide amenity for people using the local area, in the form of rest areas and similar spaces.
[5 empty] | 0 |  | 2）Local contribution by provision of facilities and functions Part of the building is equipped to provide public facilities and functions, such as meeting rooms, community halls and exhibition spaces, community centers, and community use of schools, contributing to greater activity in the community. |  |  | 1
例えば、環境教育を地域Apt民,NPO,企業と連携して行えるような地域に開放できる室があり、地域の生態系、環境の保全、エコスクール等についてSch習できる場として貢献している
[5 empty] | 0 | III. Formation of rich intermediate zones linking the building interior and exterior | 1） Formation of rich intermediate zones linking the building interior and exterior |  |  | 1
Open spaces that allow the passage of wind and light, such as courtyards, terraces, balconies, sun rooms, roofed plazas, light and air voids, and atria are skillfully linked to interior spaces.
Or, in areas where private and public spaces intersect, such as around entrances and balconies, light and air voids, flower beds, pergolas, deep balconies and similar elements have been built to form rich intermediate spaces which give a lived-in atmosphere.
[5 empty] | 0 | IV. Consideration for crime prevention | 1） Consideration for crime prevention |  |  | 1
Crime prevention performance is considered, so that in spaces outside the building, such as plazas, trees are placed to avoid blocking lines of sight, nocturnal lighting and security cameras are installed, windows are placed where they will be useful for crime prevention, and other measures are used.
Or, if there are no plazas or pedestrian walkways, consideration is given to crime prevention in the form of avoiding the creation of blind spots, such as blind alleys and paths out of lines of sight, placing windows where they will be useful for crime prevention, and other measures.
Or, if there are boundary barriers around the site, crime and disaster prevention are considered, in the form of fences or low hedges which afford clear lines of sight, rather than continuous walls or similar barriers which block lines of sight.
新築はなし |  |  |  |  | 0 | V 屋外施設等の適切な維持管理（植栽管理を除く） | 7) 屋外施設等の適切な維持管理の実施 屋外施設等（舗装,ファニチャー等）について適切な維持管理（清掃,洗浄,補修等）が実施されている。 |  |  | 1
[5 empty] | 0 | V. Participation of building users etc. | 1）Participation of building users etc. User satisfaction assessments (POE) are used to involve building users in the design process for cooperative housing etc. |  |  | 1
Or, residents and occupants work directly on plant management and cleaning activities and formulate operation plans, and are otherwise participating in the maintenance of the building.
[5 empty] | 0 | VI. Other | Other (State content) |  |  | 1
[5 empty] | Total = | 3
|  | 3.2 | Improvement of the Thermal Environment on Site
[8 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | 0 points in the table of the efforts to be evaluated.
|  |  |  | Level 2 | 1-5 points in the table of the efforts to be evaluated.
|  |  |  | ■Level 3 | 6-11 points from the table of the efforts to be evaluated.
|  |  |  | Level 4 | 12-17 points from the table of the efforts to be evaluated.
|  |  |  | Level 5 | 18 points or more in the table of the efforts to be evaluated.
Efforts to be evaluated
[5 empty] | point(s) | Assessment Item | Description |  |  | allocated point(s)
[5 empty] | 2 | I. Guide wind into the site to relieve the thermal environment | 1) The planned form and layout of buildings guides wind onto the plot. |  |  | 2
[5 empty] | 3 |  | 2) Secure paths for air movement by providing green spaces of lawn, meadow and bushes etc., and suitable spaces and paths within the plot. |  |  | 1～3
Open space ratio is 40% or more, less than 60% (1 point) 60% or more, less than 80% (2 points) 80% or more (3 points)
[5 empty] | 1 | III. Shaded space is created during the summer to alleviate thermal impact on pedestrian areas on the site | 1) Shaded areas are created with the use of medium/tall trees, piloti, eaves, pergolas, or other similar measures. |  |  | 1～3
Rate of horizontal projection area of medium and tall trees, piloti, etc. is 10% or more, less than 20% (1 point) 20% or more, less than 30% (2 points) 30% or more (3 points)
[5 empty] | 0 | III. Green and water spaces are provided to alleviate thermal impact on pedestrian areas on the site | 1)Surface and near-surface temperatures are controlled by establishing green and water spaces. Total rate of green-covered areas, water-covered areas and horizontal projection areas of medium and tall trees is |  |  | 1～3
10% or more, less than 20% (1 point) 20% or more, less than 30% (2 points) 30% or more (3 points)
[5 empty] | 0 |  | 2)Endeavor to reduce the area of paving on the plot. |  |  | 1～3
Percentage of paved area is 20% or more, less than 30% (1 point) 10% or more, less than 20% (2 points) Less than 10% (3 points)
[5 empty] | 0 | IV. Exterior finishes of the building promote alleviation of thermal impact on pedestrian areas on the site | 1) The green space plan includes accessible rooftop areas (including artificial base). |  |  | 2～3
The building has an accessible rooftop area that is partially covered with plants. (2 points) The building has an accessible rooftop area that is extensively covered with plants. (3 points)
[5 empty] | 0 |  | 2) Appropriate exterior wall materials for thermal control are used. |  |  | 1～3
Percentage of exterior walls with appropriate materials is Less than 10% (1 point) 10% or more, less than 20% (2 points) 20% or more (3 points)
[5 empty] | 0 | V. Heat vents for service equipment are appropriately located to alleviate thermal impact on pedestrian areas on the site | 1)Heat vents for main service equipment (e.g. air conditioning system) are installed in high locations. At least half of cooling towers or outdoor units generating waste heat are installed 10 meters or higher above ground level. (1 point) Most cooling towers or outdoor units generating waste heat are installed 10 meters or higher above ground level OR no units are installed. (2 points) |  |  | 1～2
[5 empty] | 0 |  | 2)High-temperature heat vents for main service equipment (e.g. combustion equipment) are installed in high locations. At least half of high-temperature heat venting units are installed 10 meters or higher above ground level. (1 point) Most high-temperature heat venting units are installed 10 meters or higher above ground level OR no units are installed. (2 points) |  |  | 1～2
[5 empty] | Total = | 6

## LR1
[11 empty] | ■Building Name | XXX Building |  | プルダウン選択肢
|  | LR1 Energy |  |  |  |  | Select from pull-down menus or enter figures and comments. | [6 empty] | <評価しない> | Yes |  | Preliminary design stage
[16 empty] | ON | Execution design stage
Construction completion stage
|  | 1 | Control of Heat Load on the Outer Surface of Buildings
Sch校版基準 | [6 empty] | Weighting coefficients(default) = | #DIV/0!
0 |  |  |  | 3 | 小中Sch校
- | 1 |  |  |  | 一般地域 |  | 寒冷地域 |  | 暑熱地域
2 | 3 |  |  | Level 1 | (該当するレベルなし) |  | (該当するレベルなし) |  | (該当するレベルなし) | [5 empty] | 1 | Level 1 | ■Level 1
3 | 3 |  |  | Level 2 | レベル３に満たない |  | レベル３に満たない |  | レベル３に満たない | [5 empty] | 2 | Level 2 | ■Level 2
4 | 4 |  |  | ■Level 3 | 厚さが20mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ複層ガラスを使用している |  | 厚さが40mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ複層ガラスを使用している |  | 熱反ガラスを使用し、且つ水平庇１．０ｍ以上が計画されている。又は、高性能熱反ガラスを使用し、かつ水平庇0.5～1.0ｍが計画されている。 | [5 empty] | 3 | Level 3 | ■Level 3
5 | 5 |  |  | Level 4 | 厚さが20mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ低放射複層ガラスを使用している |  | 厚さが40mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ低放射複層ガラスを使用している |  | 高性能熱反ガラスを使用し、且つ水平庇１．０ｍ以上が計画されている。 | [5 empty] | 4 | Level 4 | ■Level 4
0 | 0 |  |  | Level 5 | レベル４に加え、ダブルスキン等の断熱に有効な手法が採用されている。 |  | レベル４に加え、ダブルスキン等の断熱に有効な手法が採用されている。 |  | レベル４に加え、外ルーバー等の日射遮蔽に有効な手法が採用されている。 | [5 empty] | 5 | Level 5 | ■Level 5
|  |  |  | Entire Building |  |  | Weighting coefficients(default) = | #DIV/0! | [6 empty] | 0 | レベル | レベル
|  |  |  | #VALUE! | 0 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl | [6 empty] | 0
[6 empty] | Assessment based on [BPI] |  |  |  | Assessment based on the Model Building Method [BPIm]
[6 empty] | Zone 1-7 |  | Zone 8 |  | Zone 1-7 |  | Zone 8
|  |  |  | #VALUE! | Level 1 | Level 1: [BPI] ≧ 1.03 | Those that fall between the above levels are evaluated based on the BPI, utilizing the linear interpolation to the first decimal place. | Level 1: [BPI] ≧ 1.03 | Those that fall between the above levels are evaluated based on the BPI, utilizing the linear interpolation to the first decimal place. | 1.00 ＜ [BPIm] |  | 1.00 ＜ [BPIm]
|  |  |  | #VALUE! | Level 2 | Level 2: [BPI] ＝ 1.00 |  | Level 2: [BPI] ＝ 1.00 |  | 0.97 ＜ [BPIm] ≦1.00 |  | 0.97 ＜ [BPIm] ≦ 1.00
|  |  |  | #VALUE! | Level 3 | Level 3: [BPI] ＝ 0.97 |  | Level 3: [BPI] ＝ 0.97 |  | 0.90 ＜ [BPIm] ≦ 0.97 |  | 0.93 ＜ [BPIm] ≦ 0.97
|  |  |  | #VALUE! | Level 4 | Level 4: [BPI] ＝ 0.90 |  | Level 4: [BPI] ＝ 0.93 |  | [BPIm] ≦ 0.90 |  | [BPIm] ≦ 0.93
|  |  |  | #VALUE! | Level 5 | Level 5: [BPI] ≦ 0.80 |  | Level 5: [BPI] ≦ 0.85 |  | (No corresponding level) |  | (No corresponding level)
[5 empty] | Enter thermal performance grade | Apt |  |  | 0
[5 empty] | #VALUE! | Corresponding to grade 1 of the Japan Housing Performance Standard "5-1 Energy-saving Countermeasure Grade."
[5 empty] | #VALUE! | Corresponding to grade 2 of the Japan Housing Performance Standard "5-1 Energy Saving Countermeasure Grades."
[5 empty] | #VALUE! | Corresponding to grade 3 of the Japan Housing Performance Standard "5-1 Energy Saving Countermeasure Grades."
[5 empty] | #VALUE! | (No corresponding level)
[5 empty] | #VALUE! | Corresponding to grade 4 of the Japan Housing Performance Standard "5-1 Energy Saving Countermeasure Grades."
Direct entry
3
|  | 2 | Natural Energy Utilization
|  | 2.1 | 定量評価 |  |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct | [7 empty] | 0
|  |  |  | Level 1 | （該当するレベルなし） | [6 empty] | 自然エネルギーの直接利用量（採光や通風など）を評価する。太陽光発電やソーラーパネル等などの電気や熱に変換して利用するものについては、「3．設備システムの高効率化」で評価する。
|  |  |  | Level 2 | （該当するレベルなし）
|  |  |  | ■Level 3 | 0MJ/㎡,年≦ [利用量] ＜1MJ/㎡,年 ※利用なし、モニュメントの計画含む
|  |  |  | Level 4 | 1MJ/㎡,年≦ [利用量] ＜15MJ/㎡,年
|  |  |  | Level 5 | 15MJ/㎡,年≦ [利用量]
[5 empty] | 自然エネルギー直接利用量 |  | 0 | MＪ／年㎡ （変換利用量は含まない）
|  | 2.2 | 定性評価 |  |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 0 | 3 | Off,Sch（Univ., etc）, Rtl,Rst,Hal,Hsp,Htl,Fct |  | 0 | Note | 3 | Sch(ES/JHS/HS),Apt |  | 0
- | - |  |  |  | Level 1 | (No corresponding level) |  |  | Exclude usage in production rooms in Factory. | Level 1 | (No corresponding level)
- | 2 |  |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | Natural lighting and ventilation do not meet level 3.
3 | 3 |  |  |  | ■Level 3 | No measures of the assessment criteria are implemented. Although some methods are used, their effectiveness, however, has not been examined. |  |  | Factories with only production area are not applicable. | ■Level 3 | Nearly all private areas (at least 80%) of classrooms or apartments face exterior walls on two sides, ensuring effective natural lighting and ventilation.
4 | 4 |  |  |  | Level 4 | In some of the methods used as part of the efforts subject to the assessment, their effectiveness has been confirmed. (excluding monument design) |  |  | (Select "N.A." in the effort to be evaluated, below) | Level 4 | In addition to the above, building measures, such as ventilation voids, have been used to enhance efficacy. They influence a majority (50% or more) of the building.
5 | 5 |  |  |  | Level 5 | Same as level 4 and direct energy usage of 15 MJ/m2-yr or more |  |  |  | Level 5 | The above building measures cover at least 80% of the building
0 | 0
[5 empty] | Direct usage of natural energy |  | 0 | MＪ/m2-yr (exclude converted usage such as power generation by P.V.)
Applicable |  |  |  |  | NO. | Introduced effort | Efforts to be evaluated |  | Applicable | <-- Select ".N.A." for Factory with only production rooms.
0 | 0 |  |  |  | 1 |  | Use of natural light: Planning for natural light systems that use daylight in place of lighting equipment. (E.g., light shelves, top lights, high side lights, etc.)
[5 empty] | 2 |  | Use of natural ventilation: Planning for the use of natural ventilation and ventilation systems that are effective in replacing the use of air conditioning equipment and reducing cooling loads. (E.g., automatic dampers, manually operated openings and windows (those with a plan for an operational management method), night purging, ventilation systems linked to atria, solar chimney ventilation towers, etc.)
[5 empty] | 3 |  | Use of geothermal energy: Planning for the use of geothermal heat usage systems that are effective in replacing the use of heat sources and air conditioning equipment and reducing heating and cooling loads. (E.g., cool and heat tubes and pits, etc.)
[5 empty] | 4 |  | Other: Planning for the effective use of nature in other systems.
|  | 3 | Efficiency in Building Service System |  |  |  |  | #DIV/0!
|  | 3.1 | 設計仕様に基づく評価
|  |  |  | Entire Building | Other than Apt. |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 0 | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  |  |  | 0
[6 empty] | Assessment based on [BEI] |  |  | Assessment based on the Model Bldg. Method [BEIm]
|  |  |  | Level 1 | Level 1 | Level 1: [BEI] ≧ 1.10 |  | Those that fall between the above levels are evaluated based on the BEI, utilizing the linear interpolation to the first decimal place. | 1.05 ＜ [BEIm]
|  |  |  | Level 2 | Level 2 | Level 2: [BEI] ＝ 1.05 |  |  | 1.00 ＜ [BEIm] ≦ 1.05
|  |  |  | Level 3 | ■Level 3 | Level 3: [BEI] ＝ 1.00 |  |  | 0.90 ＜ [BEIm] ≦ 1.00
|  |  |  | Level 4 | Level 4 | Level 4: [BEI] ＝ 0.90 |  |  | [BEIm] ≦ 0.90
|  |  |  | Level 5 | Level 5 | Level 5: [BEI] ≦ 0.70 |  |  | (No corresponding level)
|  |  |  | Apt | [8 empty] | 0
|  |  |  | 0 | 0 | Common area |  | 0 | 0 | Private areas |  |  | 0
[6 empty] | Level 1: [BEI] ≧ 1.10 |  | Those that fall between the above levels are evaluated based on the BEI, utilizing the linear interpolation to the first decimal place. |  | Level 1: The primary energy consumption ratio is more than 130% |  |  | Those that fall between the above levels are evaluated based on the primary energy consumption ratio, utilizing the linear interpolation to the first decimal place.
[6 empty] | Level 2: [BEI] ＝ 1.05 |  |  |  | Level 2: The primary energy consumption ratio is 120%
[6 empty] | Level 3: [BEI] ＝ 1.00 |  |  |  | Level 3: The primary energy consumption ratio is 110%
[6 empty] | Level 4: [BEI] ＝ 0.90 |  |  |  | Level 4: The primary energy consumption ratio is 100% (Equivalent to the 2013 standard)
[6 empty] | Level 5: [BEI] ≦ 0.70 |  |  |  | Level 5: The primary energy consumption ratio is less than 90% (Equivalent to the low carbon standard)
Assessment that do not utilize the calculation program
Both the Standard Concerning Prevention of Heat Loss through Outer Walls and Windows and the Standard for the Primary Energy Consumption
prescribed in the Guidelines for Design, Construction, Maintenance and Conservation Concerning Rational Use of Energy in Housing
(Notification No. 907 of MLIT in 2013) are fulfilled. Level 1 is given if not.
3.2 実績値を用いた総合評価
（１） 設計仕様に基づく評価の補正
|  |  |  | 2 | [3.1a、3.1bによる設備システムの高効率化のスコア]が2.0点未満 |  |  |  | 1
[5 empty] | [3,1a、3.1bによる設備システムの高効率化のスコア]が2.0点以上 |  |  |  | スコア-1.0
（２） 実測結果に基づく評価
|  |  |  | 0 | （１）によるスコア | 加点あり | 上下なし | 減点あり
[5 empty] | 1.0以上1.5未満 | 2 | 1 | 1
[5 empty] | 1.5以上2.0未満 | 2.5 | 1.5 | 1
[5 empty] | 2.0以上2.5未満 | 3 | 2 | 1
[5 empty] | 2.5以上3.0未満 | 3.5 | 2.5 | 1.5
[5 empty] | 3.0以上3.5未満 | 4 | 3 | 2
[5 empty] | 3.5以上4.0未満 | 4.5 | 3.5 | 2.5
[5 empty] | 4 | 5 | 4 | 3
3.1 空調設備
Sch校版基準 |  |  |  | 基本設計段階 |  |  | Weighting coefficients(default) = | 0.5
0 |  |  |  | 0 | 小中Sch校 | [6 empty] | 備考
- | 1 |  |  |  | (該当するレベルなし)
2 | 3 |  |  |  | レベル３に満たない
3 | 3 |  |  |  | 冷暖房平均COPが1.25以上の熱源機器を採用
4 | 4 |  |  |  | レベル３に加え、空調対象面積の50％以上に全熱交換器を採用
5 | 5 |  |  |  | レベル４に加え、地中熱や井水、太陽熱、顕熱潜熱分離等の更なる効率化が図られている。
0 | 0
|  |  |  | 3.2 換気設備 |  | <評価しない>
3.3 照明設備
Sch校版基準 |  |  |  | 基本設計段階 |  |  | Weighting coefficients(default) = | 0.5
0 |  |  |  | 0 | 小中Sch校 | [6 empty] | 備考
- | 1 |  |  |  | (該当するレベルなし) | [6 empty] | ＜７種類の制御方式＞ カード,センサー等による在室検知制御、明るさ感知による自動点滅制御、適正照度制御（初期照度補正）、タイムスケジュール制御、昼光利用照明制御、ゾーニング制御、局所制御
2 | 3 |  |  |  | レベル３に満たない
3 | 3 |  |  |  | Hf(高周波点灯専用型）が採用されている。
4 | 4 |  |  |  | レベル３に加え、７種類のうち２種類以上採用されている。
5 | 5 |  |  |  | レベル３に加え、７種類のうち４種類以上採用されている。
0 | 0
|  |  |  | 3.4 給湯設備 |  | <評価しない>
|  |  |  | 3.5 昇降機設備 |  | <評価しない>
|  | 4 | Efficient Operation
|  | 4.1 | Monitoring |  |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  |  | 3 | Apt
- | - |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | (No corresponding level)
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | It must be possible to identify the annual consumption of each kind of energy used in the building and use the base unit for energy consumption, or other means, for benchmark comparison. |  |  |  | ■Level 3 | No efforts to be evaluated.
4 | 4 |  |  | Level 4 | Beyond level 3, the breakdown of energy consumption*1 for each major building type must be identified, trends in consumption identified and analyzed, and their appropriateness confirmed. |  |  |  | Level 4 | Equipment that indicates the amount of energy consumed, environmental-load-reducing devices and the like, are employed.
5 | 5 |  |  | Level 5 | Beyond level 4, the system efficiency*2 of major equipment systems must be evaluated in order to evaluate the performance of the systems. |  |  |  | Level 5 | A system for managing energy is established and efforts for reducing energy consumption are made therein.
0 | 0 |  |  |  | *1 Broadly, monitoring must be planned which will be able to identify the breakdown, by application, of a majority of the total energy consumption.
*2 Broadly, efficiency assessment must be performed on at least four of the types listed in table 1. If there are many systems, such as air conditioning, lighting and ventilation, it is permissible to estimate the whole from the assessment of representative systems.
Efficiency evaluation examples
|  |  |  | Equipment type |  | Evaluation item |  | Evaluation content |  |  |  | Note
|  |  |  | 1 | Heat source equipment | Heat source machine COP assessment |  | Amount of generated heat/energy consumed by the heat source (based on primary energy)/Available heat of heat storage tank/Utilization efficiency of heat storage tank
[6 empty] | COP assessment of heat source systems |  | Amount of generated heat/energy consumed by the heat source and related equipment (based on primary energy) |  |  |  | Includes introduction of district heating and cooling
[6 empty] | Heating medium conveyance WTF |  | Amount of heat carried/energy consumed by pump (based on secondary energy)
|  |  |  | 2 | Air conditioning equipment | Air conditioner conveyance ATF |  | Amount of heat carried/energy consumed by fan (based on secondary energy)
[6 empty] | Total enthalpy heat exchange effect |  | Amount of heat reduced, amount of energy
[6 empty] | Cooling effect by external air |  | Amount of heat reduced, amount of energy
[6 empty] | Multi-COP assessment for buildings |  | Efficiency in multi-split A/C system
|  |  |  | 3 | Ventilation equipment | Assessment of variable air volume control
|  |  |  | 4 | Lighting equipment | Assessment of various types of control |  | Amount of energy saved by the use of daylight, occupant sensors, etc.
|  |  |  | 5 | Hot water supply equipment | Heat source machine COP assessment |  | Amount of generated heat/energy consumed by the heat source (based on primary energy)
[6 empty] | COP assessment of heat source systems |  | Amount of generated heat/energy consumed by the heat source and related equipment (based on primary energy)
[6 empty] | Heating medium transmission WTF |  | Amount of heat carried/energy consumed by pump (based on secondary energy)
|  |  |  | 6 | Elevator | Individual control operation effect |  | Reduced energy
|  |  |  | 7 | Other | Assessment of solar power generation facility |  | Power generation efficiency/Rating efficiency/Annual efficiency
[6 empty] | CGS assessment |  | Electricity generation efficiency, overall efficiency, energy saving rate
[6 empty] | Coordinated controls |  | Lighting/ventilation on/off control linked with security sensors
[6 empty] | Other |  | A/C CO2 control effect, Ventilation CO2 control effect, Task ambient A/C effect, Task ambient lighting effect, etc.
* Using data obtained by devices with control sensors can also be applied in the efficiency evaluation.
|  | 4.2 | Operation & Management System |  |  |  |  | #DIV/0!
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  |  | 3 | Apt
1 | 1 |  |  | Level 1 | No operation and management has been planned. |  |  |  | Level 1 | No efforts to be evaluated.
2 | 2 |  |  | Level 2 | Organizations, systems or management policies have been planned for operation and management. |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | Level 3 | In addition to level 2, there must be an organized operation and management system, designated manager. |  |  |  | ■Level 3 | User manuals for individual facilities are provided to the occupants.
4 | 4 |  |  | Level 4 | In addition to level 3, target values for energy consumption in the whole buildings have been planned and presented to the building owner, based on calculation of annual energy consumption. |  |  |  | Level 4 | In addition to satisfying the requirements for Level 3, general instructions regarding an energy-saving way of living are given to the occupants.
5 | 5 |  |  | Level 5 | In addition to level 4, there must be regular verification of equipment performance during building operation, with specific actions planned for repair of malfunctions etc. (commissioning system) |  |  |  | Level 5 | In addition to satisfying the requirements for Level 3, appropriate instructions regarding the facilities and specifications installed in the subject dwelling unit, suitable for the respective building and life style, are given to the occupants.
0 | 0
1 | -
- | -
3 | 3
4 | 4
5 | 5
0 | 0
Note on F16: 住宅部分と非住宅部分の床面積による加重平均（小数第2位で切捨）
Note on F65: 住宅部分と非住宅部分の床面積による加重平均（小数第2位で切捨）
Note on F74: 専有部分と共用部分の床面積による加重平均（小数第２位で切捨）

## ENcalc
n LR1 Data from "energy-saving plan" | [9 empty] | ■Building Name | XXX Building
[14 empty] | assessment according to the BPI |  | BPI= | 5 |  | -10 | 13 | 5 |  | -12.5 | 15.625
[6 empty] | Buildings except Apartment |  |  |  | Apartment |  |  |  | assessment according to the BPIm |  | BPIm= | 4 |  |  |  | 4
1 | Performance of the outer surface of a building | [13 empty] | N.A. | BPI | レベル | Zone 1-7 | a（傾き） | ｂ（切片） | レベル | Zone 8 | a（傾き） | ｂ（切片）
|  | assessment according to the BPIm |  |  | BPIm= |  |  |  | Housing Performance Standard | [5 empty] | Grade 1 |  | 1 | 1.03 | 0 | 1 | 1 | 1.03 | 0 | 1
[15 empty] | Grade 2 |  | 2 | 1 | -33.3333 | 35.3333 | 2 | 1 | -33.3333 | 35.3333
[6 empty] | Zone 1-7 | Zone 8 | [7 empty] | Grade 3 |  | 3 | 0.97 | -33.3333 | 35.3333 | 3 | 0.97 | -33.3333 | 35.3333
|  | Level |  |  | assessment according to the BPI | 5 | 5 | [7 empty] | Grade 4 |  | 4 | 0.9 | -14.2857 | 16.8571 | 4 | 0.93 | -25 | 27.25
[5 empty] | assessment according to the BPIm | 4 | 4 | [7 empty] | Enter thermal performance grade |  | 5 | 0.8 | -10 | 13 | 5 | 0.85 | -12.5 | 15.625
|  | Climate Zone |  | 0 |  | 0 |  |  |  | Enter thermal performance grade | [5 empty] | BPIｍ | レベル | Zone 1-7 |  |  | レベル | 0
[17 empty] | 1 |  |  |  | 1
[5 empty] | Floor area | 0 | m2 (excluding factories) |  |  | 0 | m2 | [5 empty] | 2 | 1 |  |  | 2 | 1
[5 empty] | Floor area ratio | 0 |  |  |  | 0 | [6 empty] | 3 | 0.97 |  |  | 3 | 0.97
[17 empty] | 4 | 0.9 |  |  | 4 | 0.93
|  | LR1/1. Building thermal load |  |  | Entire building | #VALUE! | [10 empty] | 5 |  |  |  | 5
|  | 旧PAL低減率への換算 |  |  |  | 195 | ％ | [7 empty] | PAL*低減率 |  | 100 |  |  |  | 5 |  | 0 | 0
[17 empty] | 1～7地域 | ８地域 |  |  | レベル | PAL低減率 | a（傾き） | ｂ（切片）
[6 empty] | 5 | [9 empty] | [PAL＊低減率]＜2.5 | 200 | 200 |  |  | 1 | -5 | 0.2 | 2
[16 empty] | 2.5≦[PAL＊低減率]＜7.5 | 131.7 | 200 |  |  | 2 | 0 | 0.2 | 2
3 | Primary energy consumption of the building (Efficiency in Building Service System) | [8 empty] | Apartment | [5 empty] | 7.5≦[PAL＊低減率]＜10 | 131.7 | 264.8 |  |  | 3 | 5 | 0.1 | 2.5
|  | assessment according to the BEIm |  |  |  | Bldgs. except Apt. |  |  |  | Common area | Private area (Total of all units) |  |  |  |  | 10≦[PAL＊低減率] | 195 | 264.8 |  |  | 4 | 15 | 0.05 | 3.25
[5 empty] | BEIm= | 1 |  | Primary energy consumption ratio = |  | - | 0 | [5 empty] | 195 | 264.8 |  |  | 5 | 35
[5 empty] | BEIm (excluding on-site generation）= | 0.9 |  |  |  |  | * Excluding the power for home appliances and cooking in private areas
[6 empty] | 3 |  |  |  | 0 | 0 |  |  | assessment according to the BEI |  |  | 1 |  | -20 | 23 | 5 |  | 0 | 0
assessment according to the BEIm
[5 empty] | Floor area | 0 | m2 |  |  | 0 | 0 | m2
|  | LR1/3. Efficiency in Building Service System |  |  |  | 3 |  |  |  | 0
|  | LR1/3.2 実績値を用いた総合評価 |  |  | (1)補正 | 2
(2)実測値
0
[17 empty] | レベル | 非住宅 | a（傾き） | ｂ（切片） | レベル | 専有部 | a（傾き） | ｂ（切片）
|  | ERRへの換算 |  |  |  | 5 | ％ |  |  | #VALUE! | ％ | [5 empty] | 1 | 1.1 | -20 | 23 | 1 | 1.3 | -10 | 14
[6 empty] | 3 |  |  |  | #VALUE! |  |  |  | 1 |  |  | 2 | 1.05 | -20 | 23 | 2 | 1.2 | -10 | 14
[14 empty] | 2 |  |  | 3 | 1 | -10 | 13 | 3 | 1.1 | -10 | 14
| n Standard primary energy consumption | [5 empty] | GJ/yr |  |  |  |  | GJ/yr |  | 3 |  |  | 4 | 0.9 | -5 | 8.5 | 4 | 1 | -10 | 14
|  | Other energy consumption (for home appliances and cooking) included therein | [9 empty] | <--may be transcribed from the simple calculation below |  | 4 |  |  | 5 | 0.7 |  |  | 5 | 0.9
| n Designed primary energy consumption (1) | [12 empty] | 5
| n Designed primary energy consumption (2)* | [14 empty] | 共用部 | 1 |  | -20 | 23
| n Total energy including solar power ([3] On-site measures) | [5 empty] | GJ/yr |  |  |  |  | GJ/yr
[5 empty] | BEI(1) | - |  |  |  | - | [6 empty] | 3 |  | 0.1 | 2.5 | #VALUE! |  | 0 | 0
[5 empty] | BEI(2) | - |  |  |  | - |  |  |  |  | ERRレベル |  | レベル | 非住宅 | a（傾き） | ｂ（切片） | レベル | 共用部 | a（傾き） | ｂ（切片）
|  | *Designed primary energy consumption (2); The primary energy obtained by adding the reduced energy consumption evaluated in (3) Efforts made on-site | [14 empty] | 1 | -5 | 0.2 | 2 | 1 | -5 | 0.2 | 2
|  | (including solar power generation and the like) back to the designed primary energy consumption (1) used when obtaining the BEI in the energy saving | [14 empty] | 2 | 0 | 0.2 | 2 | 2 | 0 | 0.2 | 2
[17 empty] | 3 | 5 | 0.1 | 2.5 | 3 | 5 | 0.1 | 2.5
[17 empty] | 4 | 15 | 0.05 | 3.25 | 4 | 15 | 0.05 | 3.25
| n | Simple calculation of "Other energy (for home appliances and cooking)" required for Apartment assessment | [14 empty] | 5 | 35 |  |  | 5 | 35
[5 empty] | Floor area ratio | Gloss floor area (m2) | αM | No. of dwelling units | βM | EM | total
|  |  |  | a (Less than 30 m2) |  | 0 | 0 |  | 12181 | 0 | 0 | GJ/yr
|  |  |  | b (More than 30 m2 and less than 60 m2) |  | 0 | 87 |  | 9571 | 0
|  |  |  | c (More than 60 m2 and less than 90 m2) |  | 0 | 167 |  | 4771 | 0
|  |  |  | d (More than 90 m2 and less than 120 m2) |  | 0 | 47 |  | 15571 | 0
|  |  |  | e (More than 120 m2) |  | 0 | 0 |  | 21211 | 0
|  |  |  | total | 0
Assessed by primary energy calculation
| n When the primary energy consumption is not calculated (Entry all three colums, below) | [13 empty] | 1
|  | Level 4 is awarded when both the Standard Concerning Prevention of Heat Loss through Outer Walls and | [7 empty] | Level | Assessed by primary energy calculation |  |  |  | 4
Windows and the Standard for the Primary Energy Consumption prescribed in the Guidelines for Design, Construction,
Maintenance and Conservation Concerning Rational Use of Energy in Housing (Notification No. 907 of MLIT in 2013) are fulfilled. Level 1 is given if not.
|  | Heating | － |  |  |  | Cooling | － | [6 empty] | A | a
|  |  | A: Method in which the entire dwelling unit is heated | [5 empty] | a: Method in which the entire dwelling unit is cooled | [5 empty] | B | b
|  |  | B: Method in which only the living space is heated (Continuous heating) | [5 empty] | b: Method in which only the living space is cooled (Intermittent cooling) | [5 empty] | C | －
|  |  | C: Method in which only the living space is heated (Intermittent heating) | [5 empty] | －: Other than above (or unknown) | [5 empty] | －
－: Other than above (or unknown)
Primary energy consumption (standard calculation) used for calculating LCCO2 during operation stage
| Building-related Initiatives [2] | [9 empty] | Subject |  | Ref. bldg.
|  |  | BEI(2) |  |  |  | Reduction by natural energy |  | Reduction rate by efficient operation |  | GJ/yr |  | GJ/yr
|  | Other than Apt. | 0.9 |  |  |  | 0 | GJ/yr | #DIV/0! |  | #DIV/0! |  | 0 |  | #DIV/0!
[5 empty] | floor area |  | Primly energy consumption |  | conversion factor
[5 empty] | m2 |  | Statistic value | MJ/m2-yr | kg-CO2/MJ |  |  |  |  | electricity %
|  | Office | Office |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 90%
|  |  | Government buildings |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 83%
|  | School | Kindergartens/ nursery schools |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 71%
|  |  | ES/JHS | Hokkaido | 0 |  | 0 |  | #VALUE! |  |  |  |  | 62.3%
|  |  |  | Other area | 0 |  | 0 |  | #VALUE! |  |  |  |  | 76%
|  |  | High schools |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 74%
|  |  | Universities/ colleges |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 79%
|  | Retailers | Department, supermarkets |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 93%
|  |  | Other stores |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 92%
|  | Restaurants |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 50%
|  | Halls | Theatres/halls |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 76%
|  |  | Exhibition facilities |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 81%
|  |  | Sports facilities |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 92%
|  | Factories |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 100%
|  | Hospitals |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 65%
|  | Hotels |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 77%
|  | Other than apartment |  | Total | 0 |  | 0 | (GJ/yr） | #VALUE! | [5 empty] | 0
|  | n Direct use of natural energy |  |  | floor area
[14 empty] | 設計段階 | 1
|  |  | LR1/2.1 定量評価 |  | 0 | [5 empty] | 0 | MJ/yr㎡
|  |  |  | LR1/2. Natural Energy Utilization | m2 |  | Level 3 | Level 4 | Level 5 | Score | Reduction
|  |  |  | ES/JHS/Apt. | 0 |  | 0 | 1 | 15 | 3 | 0
|  |  |  | Other than above | 0 |  | 0 | 1 | 0 | 3 | 0 | MJ/m2-yr
|  | n Efficient operation |  |  |  |  | Level 3 | Level 4 | Level 5 | Score | Reduction
|  |  | LR1/4. Efficient Operation |  |  |  | 1 | 0.975 | 0.95 | #DIV/0! | #DIV/0!
|  | Apartment | [8 empty] | Subject |  | Ref. bldg.
[11 empty] | GJ/yr |  | GJ/yr
|  |  | Private area |  |  |  | floor area | Subject | Ref. bldg. |  | - |  | 0
[7 empty] | m2 | MJ/m2-yr | MJ/m2-yr
|  |  | LR1/3c assessed by specification energy standard |  |  |  | 0 | #N/A | #N/A
|  |  | Common area | [7 empty] | - |  | 0
Note on H57: Enter the area ratio of each house size category, to make the total become 1.

## LR2
[10 empty] | ■Building Name | XXX Building |  |  | プルダウン選択肢
|  | LR2 Resources & Materials | [5 empty] | Select from pull-down menus or enter figures and comments. | [5 empty] | Yes |  | Preliminary design stage
[15 empty] | ON | Execution design stage
|  | 1 | Water Resources | [12 empty] | Construction completion stage
|  | 1.1 | Water Saving | [10 empty] | はい
[7 empty] | Weighting coefficients(default) = | #DIV/0! | [5 empty] | いいえ
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | No systems for saving water.
- | 2 |  |  | Level 2 | (No corresponding level) | [9 empty] | 1 | Level 1 | ■Level 1
3 | 3 |  |  | ■Level 3 | Major faucets are equipped with water-saving valve. | [9 empty] | 2 | Level 2 | ■Level 2
4 | 4 |  |  | Level 4 | In addition to water-saving valve, other water-saving equipment (such as flush-mimicking sound systems, water-saving toilets) is used. | [9 empty] | 3 | Level 3 | ■Level 3
- | 5 |  |  | Level 5 | (No corresponding level) | [9 empty] | 4 | Level 4 | ■Level 4
0 | 0 | [13 empty] | 5 | Level 5 | ■Level 5
|  | 1.2 | Rain Water & Grey Water
|  |  |  | 1.2.1 Rain Water Use System |  |  |  |  | 1.2.2 Grey Water Use System | [5 empty] | 0 | レベル | レベル
1.2.1 | 1.2.2 | [5 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
小中高は既存も新築の基準 |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct
- | - |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | (No corresponding level)
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | No systems for using rain water. |  |  |  | ■Level 3 | No systems for reusing grey water.
4 | 4 |  |  | Level 4 | Rain water is used. |  |  |  | Level 4 | Grey water is reused.
5 | 5 |  |  | Level 5 | Rain water usage brings the rain water usage rate to at least 20%. |  |  |  | Level 5 | More than two types of waste water are used
0 | 0 |  |  |  | Rain water usage rate = | Rain water use (m³)
Water use (Potable water + Rain water + Waste water) (m³)
|  | 2 | Reducing Use of Non-renewable Resources
|  | 2.1 | Reducing Use of Materials
| Sch校版基準 | [10 empty] | Weighting coefficients(default) = | #DIV/0!
| 0 |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | Note |  | 0
| - |  |  | Level 1 | (No corresponding level) |  |  |  | Buildings with wood as the main structural component are excluded from this assessment. |  | Level 1
| - |  |  | Level 2 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 0 points in the table of the efforts to be evaluated. | [5 empty] | Level 2
| 3 |  |  | ■Level 3 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 1 point or more in the table of the efforts to be evaluated. | [5 empty] | Level 3
| - |  |  | Level 4 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 3 points or more in the table of the efforts to be evaluated. | [5 empty] | Level 4
| 5 |  |  | Level 5 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 5 points or more in the table of the efforts to be evaluated. | [5 empty] | Level 5
0 | 0 |  |  |  | Efforts to be evaluated
[5 empty] | point(s) | Assessment Item |  |  | Description |  |  |  | allocated point(s)
Buildings with wood as the main structural component
0 | 0 |  |  |  | 1 | Concrete strength FC and main rebar strength F of main structure (unit: N/mm2) |  |  | More than Fc = 36, and less than F = 390 |  |  |  | 1
1 | 1 | [7 empty] | More than Fc = 60, and less than F = 490 |  |  |  | 3
3 | 2 | [7 empty] | More than Fc = 100, and less than F = 590 |  |  |  | 4
4 | 3 |  |  |  | 0 |  |  |  | F = 325 or more but less than 355 |  |  |  | 1
| 4 |  |  |  |  | Steel frame strength F in main structure frame (unit: N/mm2) |  |  | F = 355 or more but less than 440 |  |  |  | 3
| 5 | [7 empty] | F = 440 or more |  |  |  | 4
| 6 |  |  |  | 0 | Other measures related to major structural elements |  |  | Use of pre-stressed concrete (which reduces material cross section, thereby reducing materials used). |  |  |  | 1
| 7 | [7 empty] | Equivalent measures. |  |  |  | 1 point each
| 8 |  |  |  | Total = | 1
9
|  | 2.2 | Continuing Use of Existing Structural Frame, etc
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level)
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | The existing building frame is not reused.
- | 4 |  |  | Level 4 | (No corresponding level)
5 | 5 |  |  | Level 5 | Existing building frame is reused.
0 | 0
|  | 2.3 | Use of Recycled Materials as Structural Materials
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Note
- | 1 |  |  | Level 1 | (No corresponding level) | [6 empty] | Describe recycled materials applied to the building when Level 5 is awarded, below.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | No recycled materials are used in the main parts for structural strength.
- | 4 |  |  | Level 4 | (No corresponding level)
5 | 5 |  |  | Level 5 | Recycled materials are used in the main parts for structural strength.
0 | 0 |  |  |  | * When a product is an Eco Mark Product or a Designated Procurement Item under Green Procurement Law, count it as one item.
No. of recycled materials and its applied part (in 10 words)
Examples of recycled materials
Material name
(1) Green procurement items (public works)
[6 empty] | Blast furnace slag aggregate |  |  | FA cement
[6 empty] | Ferronickel slag aggregate |  |  | Eco cement
[6 empty] | Copper slag aggregate |  |  | Lumber
Electric furnace oxidized slag aggregate
Blast furnace cement
(2) Wood board with Eco Mark (Product Category No. 111)
(3) Products using thinned lumber, reused and unused wood materials, etc., with Eco Mark (Product Category No. 115)
Since the list of the Designated Procurement Items are constantly updated, it is advisable to refer to the following websites prior to the assessment.
- Green Procurement Law: designated item information (MOE, temporarily unavailable as of April 2014) http://www.env.go.jp/policy/hozen/green/g-law/gpl-db/material.html
- Eco Product Net (Green Purchasing Network) http://www.gpn.jp/econet/ - Eco Mark Products Search Site (the Japan Environment Association) http://www.ecomark.jp/search/search.php
|  | 2.4 | Use of Recycled Materials as Non-structural Materials
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Note
1 | 1 |  |  | Level 1 | No recycled materials are used. | [6 empty] | Describe recycled materials applied to the building when Level 3 or higher is awarded, below.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | One type of recycled material is used.
4 | 4 |  |  | Level 4 | Two types of recycled material are used.
5 | 5 |  |  | Level 5 | Three or more types of recycled material are used.
0 | 0 |  |  |  | * When a product is an Eco Mark Product or a Designated Procurement Item under Green Procurement Law, count it as one item.
No. of recycled materials and its applied part (in 10 words)
Examples of recycled materials
Material name
Designated Procurement Items under the Green Procurement Law
[6 empty] | Recycled soil processed from construction sludge |  |  |  | Paving blocks (fired) using recycled materials materials
[6 empty] | Granulated blast furnace slag for earthworks |  |  |  | Paving blocks (precast, non-reinforced concrete) using recycled
[6 empty] | Caisson filler using copper slag |  |  |  | Ceramic tile
[6 empty] | Caisson filler using ferronickel slag |  |  |  | Lumber
[6 empty] | Steelmaking slag for ground improvement |  |  |  | Laminated wood
[6 empty] | Recycled heated asphalt mixtures |  |  |  | Plywood
[6 empty] | Asphalt mixtures with added ferrous slag |  |  |  | Laminated veneer lumber
[6 empty] | Roadbed material with added ferrous slag |  |  |  | Flooring
[6 empty] | Steel slag blocks |  |  |  | Particle board
[6 empty] | Sprayed concrete using FA |  |  |  | Wooden-type cement panels
Vinyl flooring
Tiles and blocks that have been awarded the Eco Mark (Product category No. 109)
[6 empty] | Tile |  |  |  | Brick
Block
Boards using wood materials that have been awarded the Eco Mark (Product category No. 111)
Boards
Products using thinned lumber, reused and unused materials, etc. that have been awarded the Eco Mark (Product category No. 115)
[6 empty] | Outdoor materials (Civil engineering and construction materials: Small logs) |  |  |  | Interior materials (Doors)
Exterior materials (Civil engineering and construction materials: Laminated wood)
Exterior materials (Civil engineering and construction materials: Plywood)
Exterior materials (Exterior)
[6 empty] | Interior materials (Floor materials) |  |  |  | Activated carbon (for moisture regulation)
[6 empty] | Interior materials (Wall materials) |  |  |  | Soil improvement materials
Interior materials (Sliding door frames)
Construction products (for interior decorating finishes) that have been awarded the Eco Mark (Product category No. 123)
[6 empty] | Wood flooring |  |  |  | Thermal insulation
[6 empty] | Paper screens and sliding partitions |  |  |  | Acoustic absorption materials and anti-vibration mats
[6 empty] | Paper to cover paper screens and sliding partitions |  |  |  | Vinyl floor covers
[6 empty] | Board |  |  |  | Staircase anti-slip treatment
[6 empty] | Tatami matting |  |  |  | Braille nails
[6 empty] | Wallpaper |  |  |  | Free access floor
Accordion doors
Construction products (cladding and exterior parts and materials) that have been awarded the Eco Mark (Product category No. 137)
[6 empty] | Roofing |  |  |  | Plastic decking materials
[6 empty] | Roof materials |  |  |  | Composite materials of recycled wood and plastic
Cladding materials
Construction products (material-type parts and materials) that have been awarded the Eco Mark (Product category No. 138)
[6 empty] | Construction stone |  |  |  | Sumps for residential land
Hard PVC pipes for drainage and ventilation
Since the list of the Designated Procurement Items are constantly updated, it is advisable to refer to the following websites prior to the assessment.
- Green Procurement Law: designated item information (MOE, temporarily unavailable as of April 2014) http://www.env.go.jp/policy/hozen/green/g-law/gpl-db/material.html
- Eco Product Net (Green Purchasing Network) http://www.gpn.jp/econet/ - Eco Mark Products Search Site (the Japan Environment Association) http://www.ecomark.jp/search/search.php
|  | 2.5 | Timber from Sustainable Forestry
[7 empty] | Weighting coefficients(default) = | #DIV/0!
小中高は既存も新築の基準 |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Note
- | 1 |  |  | Level 1 | (No corresponding level) | [6 empty] | N.A. if no timber is used
2 | 2 |  |  | Level 2 | Timber from sustainably managed forests is not used.
3 | 3 |  |  | ■Level 3 | Timber from sustainably managed forests supplied less than 10% of timber usage, or no timber is used, even in the structural skeleton.
4 | 4 |  |  | Level 4 | Timber from sustainably managed forests supplies 10-50% of timber usage.
5 | 5 |  |  | Level 5 | Timber from sustainably managed forests supplies 50% or more of timber usage.
0 | 0
|  | 2.6 | Efforts to Enhance the Reusability of Components and Materials
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | (No corresponding level)
|  |  |  | Level 2 | (No corresponding level)
|  |  |  | ■Level 3 | No measures, as the efforts to be evaluated, to encourage recycling of materials on demolition has been used.
|  |  |  | Level 4 | One point of measures to be evaluated, which are taken as efforts to promote material recycling on demolition, has been used.
|  |  |  | Level 5 | Two points or more of measures to be evaluated, which are taken as efforts to promote material recycling on demolition, have been used.
Efforts to be evaluated
[5 empty] | 3 | <-- Direct entry |  | Total = | 0 | item(s)
- | 1 |  |  |  | 3 | Description
- | 2 |  |  |  |  | The structure of finishing materials can be separated easily.
3 | 3 |  |  |  |  | Interior finishes and equipment are not entangled, and each can easily be removed separately for demolition, refurbishment and remodeling.
4 | 4 |  |  |  |  | Reusable unit materials are used.
5 | 5 |  |  |  |  | Structural materials or their units can easily be disassembled and reused.
0 | 0
|  | 3 | Avoiding the Use of Materials with Pollutant Content
|  | 3.1 | Use of Materials without Harmful Substances
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | (No corresponding level)
|  |  |  | Level 2 | (No corresponding level)
|  |  |  | ■Level 3 | There is no building materials to be evaluated without substances specified in the Pollutant Release and Transfer Register Law. Or the inspection has not been carried out.
|  |  |  | Level 4 | There are 1-3 building materials to be evaluated without substances specified in the Pollutant Release and Transfer Register Law.
|  |  |  | Level 5 | There are 4 or more building materials to be evaluated without substances specified in the Pollutant Release and Transfer Register Law.
[5 empty] | 3 | <-- Direct entry
- | 1 |  |  |  | Building materials to be evaluated |  |  | Total = | 0 | item(s)
- | 2 |  |  |  | Materials confirmed as specified substance free | Category |  | Building materials
3 | 3
4 | 4 |  |  |  |  | Adhesives |  | For vinyl tile floors and seating
5 | 5 | [6 empty] | For tile
0 | 0 | [6 empty] | For wallpaper
For floor board
[6 empty] | Sealants |  | For sash
For glass
For tile joint
For wall joint
[6 empty] | Waterproofing materials |  | Primer for waterproofing
For paint (surface coating)
[6 empty] | Paints |  | For fittings (wooden and metal)
For wooden parts (frames for floor and ceiling)
For structural materials
For walls
[6 empty] | Anti-corrosion treatment |  | For frames
For materials other than frames
[6 empty] | Undercoats |  | For materials for coated floors
[6 empty] | Floor coverings |  | For finishing wax
[6 empty] | Preservatives |  | For wooden parts
|  | 3.2 | Elimination of CFCs and Halons
|  |  |  | 3.2.1 Fire Retardant |  |  |  |  | 3.2.2 Foaming Agents (Insulation Materials, etc.)
[7 empty] | Weighting coefficients(default) = | #DIV/0! |  |  |  | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 4 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  | Note | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Halon flame retardants with high ODP/GWP are used (incl. critical uses). |  |  | Excluded from the assessment; buildings with no fire-extinguishing equipment, or sprinklers only, or no gas fire extinguishing facilities, foam extinguisher | Level 1 | Insulation foaming materials with ODP = 0.2 or above are used.
2 | 2 |  |  | Level 2 | Halogenated flame retardants are used. |  |  |  | Level 2 | Insulation foaming materials with ODP = 0.01-0.2 are used.
- | 3 |  |  | Level 3 | (No corresponding level) |  |  |  | ■Level 3 | Insulation foaming materials with ODP = 0.0-0.01 are used.
4 | 4 |  |  | ■Level 4 | Inert gas flame retardants are used. Or, flame retardants with 0 ODP and less than 50 GWP are used. |  |  |  | Level 4 | Insulation foaming materials with ODP=less than 0.01 and low GWP (less than 50, 100-year value) are used.
- | 5 |  |  | Level 5 | (No corresponding level) |  |  |  | Level 5 | Insulation foaming materials with zero-ODP and low GWP (100-year value is 1 or less) are used; or, no insulation foaming material used.
0 | 0
3.2.3 Refrigerants
[7 empty] | Weighting coefficients(default) = | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | Note
- | 1 |  |  | Level 1 | (No corresponding level) |  |  |  | Exclude from assessment if no refrigerant gases are used.
2 | 2 |  |  | Level 2 | HCFC is used as the refrigerant.
3 | 3 |  |  | ■Level 3 | Refrigerant of ODP = 0 is used as the refrigerant.
4 | 4 |  |  | Level 4 | Natural refrigerants and new chilling systems (ODP = 0) with GWP less than 50 are used.
- | 5 |  |  | Level 5 | (No corresponding level)
0 | 0 |  |  | Reference) Critical-uses for which halon fire retardants may be used. (Fire Prevention Notice No. 87, Hazard Notice No. 84 issued on April 28, 2005)
|  |  |  | Types of facility |  |  | Examples of facility
|  |  |  | Communications equipment etc. | Communications equipment rooms etc. |  | Communications equipment rooms, wireless equipment rooms, telephone exchange rooms, magnetic disk rooms, computer rooms, telex rooms, telephone exchange switching rooms, communications equipment control rooms, data print rooms
[5 empty] | Broadcasting studios etc. |  | TV relay rooms, remote centers, studios, lighting control rooms, musical equipment rooms, adjustment rooms, monitor rooms, broadcasting equipment rooms
[5 empty] | Control rooms etc. |  | Electrical power control rooms, operation rooms, control rooms, management rooms, disaster prevention centers, dynamometer rooms
[5 empty] | Film storages etc. |  | Film storage rooms, lighting control rooms, relay desks, VTR rooms, tape rooms, projector rooms, tape storerooms
[5 empty] | Measurement equipment rooms in hazardous material handling facilities |  | Measurement equipment rooms in hazardous material handling facilities
|  |  |  | Historical assets | Exhibition rooms etc. |  | Important cultural assets, artwork repositories, exhibition rooms, showrooms
|  |  |  | Other | Workshops etc. |  | Print rooms containing rotary presses
|  |  |  | Car parks | Car parks, etc. |  | Automated parkade, mechanical parkade (where drivers enter fire-protected areas))
Foaming agents used in expanded plastic insulating materials
|  |  |  | Types of expanded insulation materials |  |  | Period of use | Foaming agent name |  | ODP | GWP (100-year value)
|  |  |  | Urethane foam |  |  | Before 1995 | CFC-11 |  | 1 | 4750
[7 empty] | Start of 2000s | HCFC-141b |  | 0.11 | 725
|  |  |  | Urethane modified isocyanurate foam |  |  | Next generation | HFC-134a |  | 0 | 1430
[8 empty] | HFC-245fa |  | 0 | 560
[8 empty] | Cyclopentane C5H10 |  | 0 | 3
|  |  |  | Styrene olefin foam |  |  | Before 1995 | CFC-12 |  | 1 | 10900
[7 empty] | Start of 2000s | HCFC-142b |  | 0.065 | 2310
[7 empty] | Next generation | HFC-134a |  | 0 | 1430
|  |  |  | Phenol foam |  |  | Before 1995 | CFC-113 |  | 0.8 | 6130
[7 empty] | Since 2000 | Dichloromethane CH2Cl2 |  | 0
ODP and GWP values of foaming gases
|  |  |  | Substance | Persistence in atmosphere | ODP (CFC standard) | GWP (CO2 standard) 100 years | Note
|  |  |  | CFC－11 | 50 | 1 | 4750 | Level 1 (chlorofluorocarbon)
|  |  |  | CFC－12 | 120 | 1 | 10900
|  |  |  | CFC－113 | 85 | 0.8 | 6130
|  |  |  | CFC－114 | 300 | 1 | 10000
|  |  |  | CFC－115 | 1700 | 0.6 | 7370
|  |  |  | HCFC－22 | 13.3 | 0.055 | 1810 | Level 2
|  |  |  | HCFC－123 | 1.4 | 0.02～0.06 | 77 | (Hydrochlorofluorocarbon)
|  |  |  | HCFC－124 | 5.9 | 0.022 | 609
|  |  |  | HCFC－141b | 9.4 | 0.11 | 725
|  |  |  | HCFC－142b | 19.5 | 0.065 | 2310
|  |  |  | HCFC－225ca | 2.5 | 0.25 | 122
|  |  |  | HCFC－225cb | 2.6 | 0.033 | 595
|  |  |  | HFC－23 | 264 | 0 | 14800 | Level 3 (Hydrofluorocarbon)
|  |  |  | HFC－32 | 5.6 |  | 675
|  |  |  | HFC－125 | 32.6 |  | 3500
|  |  |  | HFC－134a | 14.6 |  | 1430
|  |  |  | HFC－143a | 48.3 |  | 4470
|  |  |  | HFC－152a | 1.5 |  | 124
|  |  |  | HFC－227ea | 36.5 |  | 3220
|  |  |  | HFC－236fa | 209 |  | 9810
|  |  |  | HFC－245ca | 6.6 |  | 560
|  |  |  | FC－14 | 50000 | 0 | 6500 | Level 3
|  |  |  | FC－116 | 10000 |  | 9200
|  |  |  | FC－218 | 2600 |  | 7000
|  |  |  | FC－C318 | 3200 |  | 8700

## LR3
[11 empty] | ■Building Name | XXX Building
|  | LR3 Off-site Environment | [5 empty] | Select from pull-down menus or enter figures and comments. | [5 empty] | プルダウン選択肢 |  |  | Preliminary design stage
[14 empty] | 0 |  | ON | Execution design stage
|  | 1 | Consideration of Global Warming | [10 empty] | 1 |  |  | Construction completion stage
[6 empty] | Weighting coefficients(default) = |  | #DIV/0! | [5 empty] | 2
|  |  |  | 0 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [8 empty] | N.A.
|  |  |  | Level 1 | Level 1: Lifecycle CO2 emission rate is 125% or more of the reference value. | [8 empty] | -
|  |  |  | Level 2 | [6 empty] | Those that fall between the above levels are evaluated based on the LCCO2 emission rate, utilizing the linear interpolation to the first decimal place.
|  |  |  | Level 3 | Level 3: Lifecycle CO2 emission rate is 100% of the reference value. | [9 empty] | 1 | Level 1 | ■Level 1
|  |  |  | Level 4 | [10 empty] | 2 | Level 2 | ■Level 2
|  |  |  | Level 5 | Level 5: Lifecycle CO2 emission rate is 50% or less of the reference value. | [9 empty] | 3 | Level 3 | ■Level 3
[5 empty] | Estemated LCCO2 |  |  |  | kg-CO2/m2-yr | [5 empty] | 4 | Level 4 | ■Level 4
[6 empty] | Construction | Repair, Renewal and Demolition | Operation | Total | Emission rate |  |  | Converted score based on LCCO2 emission rate |  | 5 | Level 5 | ■Level 5
[5 empty] | Reference | 0 | 0 | 0 | 0 | 100% |  | Converted score = | 0 |  | 0 | レベル | レベル
[5 empty] | Subject | 0 | 0 | 0 | 0 | #DIV/0! |  |  |  | N.A.
|  | 2 | Consideration of Local Environment
|  | 2.1 | Air Pollution
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Gas and dust concentrations at sources of NOx, SOx and dust exceeds the emission standards set by the Air Pollution Control Law, the Guidelines for Small Capacity Low NOx Combustors (MOE) or local ordinances.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Gas and dust concentrations at sources of NOx, SOx and dust are reduced to below the emission standards*1 set by the Air Pollution Control Law, the Guidelines for Small Capacity Low NOx Combustors (MOE) or local ordinances.
4 | 4 |  |  | Level 4 | Gas and dust concentrations at sources of NOx, SOx and dust are considerably reduced to below the emission standards*2 set by the Air Pollution Control Law, the Guidelines for Small Capacity Low NOx Combustors (MOE) or local ordinances.
5 | 5 |  |  | Level 5 | No incineration equipment is used, and absolutely no atmospheric pollutants leave the virtual enclosed space boundary of the building to the outside.
0 | 0
|  | 2.2 | Heat Island Effect
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | 0 points in the table of the efforts to be evaluated. |  | 0 points in the table of the efforts to be evaluated.
|  |  |  | Level 2 | 1-5 point(s) in the table of the efforts to be evaluated.
|  |  |  | ■Level 3 | 6-12 points in the table of the efforts to be evaluated.
|  |  |  | Level 4 | 13-19 points in the table of the efforts to be evaluated.
|  |  |  | Level 5 | 20 points or more in the table of the efforts to be evaluated.
Efforts to be evaluated
[5 empty] | point(s) | Assessment Item |  |  | Description |  |  |  | allocated point(s)
[5 empty] | 2 | I. Preliminary investigation of heat environment | 1) Preliminary investigation of the local heat environment |  | [1] Existing data such as data from nearby meteorological stations and regional meteorological observation data (AMEDAS data) was used to identify the wind environment, including directions, speeds and prevailing direction. (1 point) |  |  |  | 1～2
既存なし | [8 empty] | [2] In addition to [1] above, on-site measurements were taken, or a supplementary detailed investigation was performed using a wide-area environmental forecasting system based on wide-area meteorological data and topographical data. (2 points)
[5 empty] | 2 | II. Thermal impact reduction in surrounding area | 2) Thermal impact reduction in surrounding area by facilitating the flow of air toward downwind areas |  | [1] Position and shape of the building are arranged in the planning to promote the flow of air downwind. |  |  |  | 1～2
The building has no practical impact on the flow of air downwind: 1 point The building does not obstruct the flow of air downwind: 2 points
[5 empty] | 2 |  |  |  | [2] Exposed area of the building facing the prevailing summer winds is reduced. |  |  |  | 1～3
Exposed area facing the prevailing wind direction is: 60% or more but less than 80%: 1 point 40% or more but less than 60%: 2 points Less than 40%: 3 points
[5 empty] | 0 |  |  |  | [3] Height, shape and spacing of building are arranged to recover the flow of air. |  |  |  | 1～3
Building spacing index Rw is: 0.3 or more but less than 0.4: 1 point 0.4 or more but less than 0.5: 2 points 0.5 or more: 3 points
[5 empty] | 0 |  | 3) Consider ground surface coverage to reduce thermal impact beyond the site |  | [1] Ground covering materials are used to reduce thermal impact. |  |  |  | 1～3
Percentage of ground covered with appropriate materials is: 15% or more but less than 30%: 1 point 30% or more but less than 45%: 2 points 45% or more: 3 points
[5 empty] | 0 |  | 4) Consider the building cladding materials to reduce thermal impact beyond the site |  | [1] Rooftop greenery system or high reflective roof material is used to reduce thermal impact. |  |  |  | 1～3
Percentage of roof covered with appropriate system/material is: Less than 20%: 1 point 20% or more but less than 40%: 2 points 40% or more: 3 points
[5 empty] | 0 |  |  |  | [2] Appropriate exterior wall materials are used to reduce thermal impact. |  |  |  | 1～3
Percentage of exterior walls covered with appropriate material is: Less than 10%: 1 point 10% or more but less than 20%: 2 points 20% or more: 3 points
[5 empty] | 0 |  | 5) Reduce atmospheric emission of heat from building equipment |  | [1] Appropriate measures to prevent heat loss via exterior walls/windows and to improve energy efficiency for A/C systems have been implemented. |  |  |  | 1～3
Score (results) in the "LR1 Energy" assessment is: 3.0 or more but less than 4.0: 1 point 4.0 or more but less than 4.5: 2 points 4.5 or more: 3 points
[5 empty] | 0 |  |  |  | [2] Air temperature increase is reduced by measures such as cooling of waste heat emitted from building service systems. |  |  |  | 1～3
Measures established to control air temperature increase are: at standard level: 1 point at intermediate level: 2 points at advanced level: 3 points
[5 empty] | 0 | III. Confirmation of effects | 6) Use simulations or other means to confirm effects in mitigating deterioration of the heat environment |  | [1] Building form and positioning, relative to wind direction, were considered at the desk plan stage (desktop prediction). (1 point) |  |  |  | 1～2
[2] Numerical simulation of fluid flow, or other methods, was used for the current situation and the planned building, considering topography of the site area, the building and surrounding green space, to predict impact. (2 points)
[5 empty] | Total = | 6
|  | 2.3 | Load on Local Infrastructure
2.3.1 Reduction of Rain water Discharge Loads
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt <If there are administrative guidelines> | [6 empty] | If there are no administrative guideline
- | 1 |  |  | Level 1 | (No corresponding level) | [6 empty] | N.A.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Rain water flow suppression measures are implemented at the instructed scale.
4 | 4 |  |  | Level 4 | The instructed scale is satisfied, and other rain water treatment measures have been implemented.
- | 5 |  |  | Level 5 | (No corresponding level)
0 | 0
2.3.2 Sewage Load Suppression
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level)
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | The Water Pollution Control Law, the Sewerage Law or the discharge standards set by local authorities etc., whichever is the most stringent, is satisfied.
4 | 4 |  |  | Level 4 | Discharge standards are satisfied, and further special measures have been used for better control of sewage loads.
- | 5 |  |  | Level 5 | (No corresponding level)
0 | 0
2.3.3 Traffic Load Control
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | 0 points in the table of the efforts to be evaluated.
|  |  |  | Level 2 | 1 point in the table of the efforts to be evaluated.
|  |  |  | ■Level 3 | 2 points in the table of the efforts to be evaluated.
|  |  |  | Level 4 | 3 points in the table of the efforts to be evaluated.
|  |  |  | Level 5 | 4 points or more in the table of the efforts to be evaluated.
Efforts to be evaluated
[5 empty] | point(s) | Assessment Item |  |  | Description |  |  |  | allocated point(s)
[5 empty] | 1 | I. Efforts related to use of bicycles (use of alternative means of transport) |  |  | 1) Provision of an appropriate number of cycle parking spaces (including motorcycle spaces) for building users, and consideration for the convenience of cycle park users (ease of entry and egress, placement in a convenient location, etc.). |  |  |  | 1
[5 empty] | 0 |  |  |  | 2) Other (state content) |  |  |  | 1
[5 empty] | 1 | II .Efforts to provide car parking space |  |  | 1) Provision of an appropriate number of car parking spaces (as a measure to avoid parking on roads, and congestion of nearby roads). |  |  |  | 1
[5 empty] | 0 |  |  |  | 2) Provision of parking facilities for unloading goods vehicles (residential buildings are not applicable). |  |  |  | 1
[5 empty] | 0 |  |  |  | 3) Consideration of the position, form and number of parking lot approach roads (entry and exit) (to contribute to relieving congestion of local roads). |  |  |  | 1
[5 empty] | N.A. |  |  |  | 4) Other (state content) |  |  |  | 1
[5 empty] | Total = | 2
2.3.4 Waste Treatment Loads
既存はAptの基準あり | [5 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | Apt
|  |  |  | Level 1 | 1 point or less in the table of the efforts to be evaluated.
|  |  |  | Level 2 | 2 points in the table of the efforts to be evaluated.
|  |  |  | ■Level 3 | 3 points in the table of the efforts to be evaluated.
|  |  |  | Level 4 | 4 points in the table of the efforts to be evaluated.
|  |  |  | Level 5 | 5 points or more in the table of the efforts to be evaluated.
Efforts to be evaluated
[5 empty] | point(s) | Assessment Item |  |  | Description |  |  |  | allocated point(s)
[5 empty] | 1 | I. Estimation of types and quantities of waste |  |  | 1) The types and quantities of waste generated on the site (interior and exterior) on a day-to-day basis have been estimated to assist in planning measures to reduce the waste processing load. |  |  |  | 1
[5 empty] | 1 | II. Provision of space and equipment to encourage separate collection |  |  | 2) Interior and exterior stock space has been planned that will allow sorted collection of many varieties of waste. |  |  |  | 1
[5 empty] | 1 |  |  |  | 3) Interior and exterior waste sorting and collection containers and boxes have been planned. |  |  |  | 1
[5 empty] | 0 |  |  |  | 4) Planned collection of valuable materials has been planned (group collections, etc.). |  |  |  | 1
新築なし |  |  |  |  | 0 |  |  |  | 5)年間の廃棄Rtlの再利用率が 50％以上75％未満である場合 1ポイント 75％以上である場合 2ポイント |  |  |  | 1～2
[5 empty] | 0 | III. Installation of equipment for waste reduction, compaction or composting |  |  | 5) Measures are planned to reduce, compact and compost organic garbage (home processing and composting etc. of organic waste). |  |  |  | 1
[5 empty] | 0 |  |  |  | 6) Reduction and compaction of bottles, cans etc. are planned. |  |  |  | 1
[5 empty] | Total = | 3
|  | 3 | Consideration of Surrounding Environment
|  | 3.1 | Noise, Vibration & Odor
3.1.1 Noise
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Note
1 | 1 |  |  | Level 1 | Noise level exceeds the current regulation standard*1 specified under the Noise Regulation Law or the Large-Scale Retail Stores Location Law. | [6 empty] | Designated facilities regulated within the designated area under the Noise Regulation Law and buildings subject to the regulation under the Large-Scale Retail Stores Location Law are considered. All other buildings are considered as level 3
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Noise level is at or below the current regulation standard*1 specified under the Noise Regulation Law or the Large-Scale Retail Stores Location Law.
- | 4 |  |  | Level 4 | (No corresponding level)
5 | 5 |  |  | Level 5 | Noise level is significantly below*2 the current regulation standard*1 specified under the Noise Regulation Law or the Large-Scale Retail Stores Location Law.
0 | 0 |  |  | *1 Take the current values of the regulation standard, and evaluate facilities accordingly, even if they were installed before the current values came into effect (evaluate for day, morning, evening and night). *2 Level 5 applies to noise level at or below [current standard value -10 dB] throughout the day.
Standard noise levels specified under the Noise Regulation Law
A condition of assessment is that the standards must be satisfied for all the measurement times, namely day (8am - 7pm), morning and evening (6am - 8am, 7pm - 10pm) and night (10pm - 6am).
[5 empty] | Type 1 zones |  |  | Type 2 zones
[5 empty] | Day | Morning & evening | Night | Day | Morning & evening | Night
|  |  |  | Level 1 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3
Level 2
|  |  |  | Level 3 | Not exceeding 45 dB | Not exceeding 40 dB | Not exceeding 40 dB | Not exceeding 50 dB | Not exceeding 45 dB | Not exceeding 45 dB
Level 4
|  |  |  | Level 5 | Not exceeding 35 dB | Not exceeding 30 dB | Not exceeding 30 dB | Not exceeding 40 dB | Not exceeding 35 dB | Not exceeding 35 dB
[5 empty] | Type 3 zones |  |  | Type 4 zones
[5 empty] | Day | Morning & evening | Night | Day | Morning & evening | Night
|  |  |  | Level 1 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3
Level 2
|  |  |  | Level 3 | Not exceeding 60 dB | Not exceeding 55 dB | Not exceeding 50 dB | Not exceeding 70 dB | Not exceeding 60 dB | Not exceeding 55 dB
Level 4
|  |  |  | Level 5 | Not exceeding 50 dB | Not exceeding 45 dB | Not exceeding 40 dB | Not exceeding 60 dB | Not exceeding 50 dB | Not exceeding 45 dB
3.1.2 Vibration
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Note
1 | 1 |  |  | Level 1 | Vibration level exceeds the current regulation standard*1 specified under the Vibration Regulation Law. | [6 empty] | The assessment is carried out regarding buildings that have designated facilities regulated within the designated area under the Vibration Regulation Law. All other buildings are excluded from this assessment.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Vibration level is at or below the current regulation standard*1 specified under the Vibration Regulation Law.
- | 4 |  |  | Level 4 | (No corresponding level)
5 | 5 |  |  | Level 5 | Vibration level is significantly below*2 the current regulation standard*1 specified under the Vibration Regulation Law.
0 | 0 |  |  | *1 Take the current values of the regulation standard, and evaluate facilities accordingly, even if they were installed before the current values came into effect (evaluate for both day and night). *2 For level 5, vibration should be limited to below [current standard value -5 dB] (for both day and night).
Standard Values from the Vibration Regulation Law
A condition of assessment is that the standards must be satisfied for all the measurement times, namely day (8am ~ 7pm) and night (7pm ~ 8am).
[5 empty] | Type 1 zones |  |  | Type 1 zones
[5 empty] | Day | Night |  | Day | Night
|  |  |  | Level 1 | Not adequate for level 3 | Not adequate for level 3 |  | Not adequate for level 3 | Not adequate for level 3
Level 2
|  |  |  | Level 3 | Not exceeding 60 dB | Not exceeding 55 dB |  | Not exceeding 65 dB | Not exceeding 60 dB
Level 4
|  |  |  | Level 5 | Not exceeding 55 dB | Not exceeding 50 dB |  | Not exceeding 60 dB | Not exceeding 55 dB
3.1.3 Odor
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Note
1 | 1 |  |  | Level 1 | Odor level is below the allowable limit for odor index, and for the concentrations of currently designated malodorous substances under the Offensive Odor Control Law. | [6 empty] | Evaluate buildings within the regulated areas as specified under the Offensive Odor Control Law and buildings in which designated malodorous substances are handled. Buildings in which such substances are not handled are excluded from this assessment.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Odor level satisfies the allowable limit for odor index, and for the concentrations of currently designated malodorous substances under the Offensive Odor Control Law.
- | 4 |  |  | Level 4 | (No corresponding level)
- | 5 |  |  | Level 5 | (No corresponding level)
0 | 0
|  | 3.2 | Wind/Sand Damage & Daylight Obstruction
3.2.1 Restriction of Wind Damage
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Note
1 | 1 |  |  | Level 1 | No preliminary study or was performed about the creation of strong wind spots*1 and no countermeasures*2 were taken against wind hazard. | [6 empty] | In the absence of a mandate based on law, regulation of administrative instruction, or of demands from the local area, building which apply no particular measures should be awarded level 3.
2 | 2 |  |  | Level 2 | A preliminary study has been performed and measures taken to avoid or reduce wind hazard, but there has been no assessment. Alternatively, wind strength grade has been evaluated on the basis of a desktop forecast*3, and wind strength has been worsened in some areas, or there are measurement points at which the wind environment rank for the sight has been lowered.
3 | 3 |  |  | ■Level 3 | A preliminary study has been performed and measures taken to avoid or reduce wind hazard*4. Then, the wind strength grade has been evaluated on the basis of a desktop forecast*3, and the results show that wind strength has not worsened. Alternatively, rank assessment has been performed on the basis of wind environment assessment indices*5, and the results indicate that a wind environment with suitable rank for the location has been achieved.
4 | 4 |  |  | Level 4 | A preliminary study or prevention planning has been performed and measures taken to avoid or reduce wind hazard, followed by a rank assessment*5 has been performed on the basis of wind environment assessment indices. Results indicate that the wind environment in some parts is better than usual for the location.
5 | 5 |  |  | Level 5 | A preliminary study or prevention planning has been performed and measures taken to avoid or reduce wind hazard, followed by a rank assessment*5 has been performed on the basis of wind environment assessment indices. Results indicate that the wind environment is better than usual for the location.
0 | 0
3.2.2 Sand and Dust
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Sch(ES/JHS/HS)
- | 1 |  |  | Level 1 | (0 points)
2 | 2 |  |  | Level 2 | Insufficient level of measures for schoolyard dust control are established. (1 point)
3 | 3 |  |  | ■Level 3 | Standard level of measures for schoolyard dust control are established. (2 points)
4 | 4 |  |  | Level 4 | More than sufficient level of measures for schoolyard dust control are established. (3 points)
5 | 5 |  |  | Level 5 | A high level of measures for schoolyard dust control are established. (4 points or higher)
0 | 0 |  |  |  | Efforts to be evaluated
[5 empty] | point(s) | Assessment Item |  |  | Description |  |  |  | allocated point(s)
[5 empty] | 2 | I. Measures to control airborne dispersion of dust from schoolyard |  |  | 1) Dust shield trees or nets surrounding the school perimeter. |  |  |  | 1
[9 empty] | 2) Structures surrounding the school perimeter. |  |  |  | 2
[5 empty] | 0 | II. Dust-proofing measures for schoolyard surface |  |  | 1) Sprinkler system |  |  |  | 1
[9 empty] | 2) Dust-proof paving |  |  |  | 2
[9 empty] | 3) Dust-proof paving/lawn covering |  |  |  | 4
[5 empty] | Total = | 2
3.2.3 Restriction of Daylight Obstruction
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level)
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Shade regulations are satisfied, or there are no shade regulations applicable to the site.
4 | 4 |  |  | Level 4 | A standard one rank* above the shade regulations is satisfied.
- | 5 |  |  | Level 5 | (No corresponding level)
0 | 0 |  |  | * "One rank above" for daylight obstruction means that, for example, in an area where the shade regulation limits shade on adjacent commercial areas to 5 hours/3 hours (at 5 m, 10 m), the next higher standard is for residential areas, set at 4/2.5 hours. If the strictest level or regulation is already applied, one rank above should be taken to mean one hour/0.5 hours (5 m, 10 m) higher than the regulation standard.
|  | 3.3 | Light Pollution
3.3.1 Outdoor Illumination and Light that Spills from Interiors
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
|  |  |  | Level 1 | 0 points in the table of the efforts to be evaluated.
|  |  |  | Level 2 | 1 point in the table of the efforts to be evaluated.
|  |  |  | ■Level 3 | 2 points in the table of the efforts to be evaluated.
|  |  |  | Level 4 | 3 points in the table of the efforts to be evaluated.
|  |  |  | Level 5 | 4 points in the table of the efforts to be evaluated.
Efforts to be evaluated
[5 empty] | point(s) | Description | [6 empty] | allocated point(s)
[5 empty] | 2 | 1) Outdoor illumination and light that spills from interiors | [6 empty] | 1～2
Only some of the checklist points of the "Light Pollution Countermeasure Guidelines" are satisfied. (1 point)
A majority of the checklist points of the "Light Pollution Countermeasure Guidelines" are satisfied. (2 points)
[5 empty] | 0 | 2) Countermeasures against light pollution from billboard lighting | [6 empty] | 1～2
Billboard lighting satisfies some of the considerations in "Considerations for Billboard Illumination." (1 point)
A majority of the considerations in "Considerations for Billboard Illumination" are satisfied, or there is no billboard lighting. (2 points)
[5 empty] | Total = | 2
3.3.2 Measures for Reflected Solar Glare from Building Walls
[6 empty] | Weighting coefficients(default) = |  | #DIV/0!
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level)
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Not adequate for Level 4.
4 | 4 |  |  | Level 4 | Measures for reducing reflected glare from building walls (including glass surfaces) are taken.
5 | 5 |  |  | Level 5 | In addition to efforts required for Level 4, further advanced measures such as confirming a significant reduction effect due to simulation practice are taken.
0 | 0

## CO2calc
CASBEE for Building (New Construction) 2014 Edition | [8 empty] | n Manual: | CASBEE for Building (New Construction) 2014 Edition
XXX Building | [8 empty] | n Software: | CASBEE-BD_NCe_2014(v.2.1)
Life Cycle CO2 Calculation Sheet （For Standard calculation）
[9 empty] | Subject |  | Reference |  | S | RC | SRC | Wood
1. CO2 Emissions Related to Construction | [12 empty] | LCCO2用床面積 |  | 合計 | 0
| 1-1. Conversion of Assessment Results to CO2 emission | [5 empty] | kg-CO2/m2-yr |  | kg-CO2/m2-yr |  | kg-CO2/m2-yr |  | Offices | 0
|  | Q2/2.2.1 Service Life of Structural Frame Materials |  | Floor area composition | Level 3 | Level 4 | Level 5 | Score | CO2 Emissions | Score | CO2 Emissions |  | 0 | 0
|  |  | Offices | 0 | 14.005 | 14.005 | 14.005 | 3 | 14.005 | 3 | 14.005 |  | Schools | 0
|  |  | Schools | 0 | 10.473 | 10.473 | 10.473 | 3 | 10.473 | 3 | 10.473 |  | 0 | 0 |  |  | Sch
|  |  | Retailers | 0 | 16.572 | 16.572 | 16.572 | 3 | 16.572 | 3 | 16.572 |  | 0 | 0 |  |  | #DIV/0!
|  |  | Restaurants | 0 | 16.572 | 16.572 | 16.572 | 3 | 16.572 | 3 | 16.572 |  | 0 | 0
|  |  | Halls | 0 | 11.535 | 11.535 | 11.535 | 3 | 11.535 | 3 | 11.535 |  | 0 | 0
|  |  | Factories | 0 | 19.562 | 19.562 | 19.562 | 3 | 19.562 | 3 | 19.562 |  | Retailers | 0
|  |  | Hospitals | 0 | 10.405 | 10.405 | 10.405 | 3 | 10.405 | 3 | 10.405 |  | 0 | 0
|  |  | Hotels | 0 | 11.119 | 11.119 | 11.119 | 3 | 11.119 | 3 | 11.119 |  | Restaurants | 0
|  |  | Apartments | 0 | 15.641 | 7.821 | 5.214 | 3 | 15.641 | 3 | 15.641 |  | Halls | 0
[13 empty] | 0 | 0
|  | Structure |  | S | [8 empty] | 0 | 0
|  | LR2/2.2 Continuing Use of Existing Building Skeleton etc. |  | 0% | [5 empty] | 0% |  |  | Factories | 0 | m2 energy saving plan | 0
|  | LR2/2.3 Use of Recycled Materials as Structural Frame Materials（Blast furnace cement (concrete)） |  | 0% | [5 empty] | 0% |  |  | Hospitals | 0
[13 empty] | Hotels | 0
| 1-2. Subtotal | [7 empty] | 0 |  | 0 |  | Non-residential Subtotal | 0
[13 empty] | Apartments | 0
| 建物寿命 |  | Offices | 0 | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Schools | 0 | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Retailers | 0 | 30 | 30 | 30 | 3 | 0 | 3 | 0
|  |  | Restaurants | 0 | 30 | 30 | 30 | 3 | 0 | 3 | 0
|  |  | Halls | 0 | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Factories | 0 | 30 | 30 | 30 | 3 | 0 | 3 | 0
|  |  | Hospitals | 0 | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Hotels | 0 | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Apartments | 0 | 30 | 60 | 90 | 3 | 0 | 3 | 0
| 代表的な資材量 |  |  |  |  | LR2/2.2 既存建築躯体 | LR2/2.3 ﾘｻｲｸﾙ材（高炉セメント）
|  | 事務所 |  | 0 | 0.567 | 0 | 0 |  | 0.567 |  | 0.567 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.567 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.136 | 0 | 0.136 |  | 0.136 |  | 0.136 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.07 | 0 | 0.07 |  | 0.07 |  | 0.07 | ｔ/㎡
|  |  |  | 0 | 0.005 | 0 | 0.005 |  | 0.005 |  | 0.005 | ｔ/㎡
|  | 学校 |  | 0 | 0.352 | 0 | 0 |  | 0.352 |  | 0.352 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.352 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.105 | 0 | 0.105 |  | 0.105 |  | 0.105 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.045 | 0 | 0.045 |  | 0.045 |  | 0.045 | ｔ/㎡
|  |  |  | 0 | 0.002 | 0 | 0.0024 |  | 0.002 |  | 0.002 | ｔ/㎡
|  | 物販店 |  | 0 | 0.342 | 0 | 0 |  | 0.342 |  | 0.342 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.342 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.072 | 0 | 0.072 |  | 0.072 |  | 0.072 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.024 | 0 | 0.024 |  | 0.024 |  | 0.024 | ｔ/㎡
|  |  |  | 0 | 0.002 | 0 | 0.00186 |  | 0.002 |  | 0.002 | ｔ/㎡
|  | 飲食店 |  | 0 | 0.342 | 0 | 0 |  | 0.342 |  | 0.342 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.342 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.072 | 0 | 0.072 |  | 0.072 |  | 0.072 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.024 | 0 | 0.024 |  | 0.024 |  | 0.024 | ｔ/㎡
|  |  |  | 0 | 0.002 | 0 | 0.00186 |  | 0.002 |  | 0.002 | ｔ/㎡
|  | 集会所 |  | 0 | 0.345 | 0 | 0 |  | 0.345 |  | 0.345 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.345 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.139 | 0 | 0.139 |  | 0.139 |  | 0.139 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.04 | 0 | 0.04 |  | 0.04 |  | 0.04 | ｔ/㎡
|  |  |  | 0 | 0.004 | 0 | 0.00435 |  | 0.004 |  | 0.004 | ｔ/㎡
|  | 工場 |  | 0 | 0.354 | 0 | 0 |  | 0.354 |  | 0.354 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.354 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.088 | 0 | 0.088 |  | 0.088 |  | 0.088 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.031 | 0 | 0.031 |  | 0.031 |  | 0.031 | ｔ/㎡
|  |  |  | 0 | 0.002 | 0 | 0.0021 |  | 0.002 |  | 0.002 | ｔ/㎡
|  | 病院 |  | 0 | 0.317 | 0 | 0 |  | 0.317 |  | 0.317 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.317 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.074 | 0 | 0.074 |  | 0.074 |  | 0.074 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.034 | 0 | 0.034 |  | 0.034 |  | 0.034 | ｔ/㎡
|  |  |  | 0 | 0.002 | 0 | 0.002 |  | 0.002 |  | 0.002 | ｔ/㎡
|  | ホテル |  | 0 | 0.436 | 0 | 0 |  | 0.436 |  | 0.436 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.436 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.103 | 0 | 0.103 |  | 0.103 |  | 0.103 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.034 | 0 | 0.034 |  | 0.034 |  | 0.034 | ｔ/㎡
|  |  |  | 0 | 0.005 | 0 | 0.00471 |  | 0.005 |  | 0.005 | ｔ/㎡
|  | 集合住宅 |  | 0 | 0.323 | 0 | 0 |  | 0.323 |  | 0.323 | ｍ3/㎡
|  |  |  | 0 | 0 | 0 | 0.323 |  | 0 |  | 0 | ｍ3/㎡
|  |  |  | 0 | 0.048 | 0 | 0.048 |  | 0.048 |  | 0.048 | ｔ/㎡
|  |  |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | ｔ/㎡
|  |  |  | 0 | 0.019 | 0 | 0.019 |  | 0.019 |  | 0.019 | ｔ/㎡
|  |  |  | 0 | 0.002 | 0 | 0.00198 |  | 0.002 |  | 0.002 | ｔ/㎡
| ◆ | 合計 | [6 empty] | 0 |  | 0 | ｍ3/㎡
[9 empty] | 0 |  | 0 | ｍ3/㎡
[9 empty] | 0 |  | 0 | ｔ/㎡
[9 empty] | 0 |  | 0 | ｔ/㎡
[9 empty] | 0 |  | 0 | ｔ/㎡
[9 empty] | 0 |  | 0 | ｔ/㎡
2. CO2 Emissions Related to Repair, Renewal and Demolition
| 2-1. Conversion of Assessment Results to CO2 emission | [5 empty] | kg-CO2/m2-yr |  | kg-CO2/m2-yr |  | kg-CO2/m2-yr
|  | Q2/2.2.1 Service Life of Structural Frame Materials |  | Floor area composition | Level 3 | Level 4 | Level 5 | Score | CO2 Emissions | Score | CO2 Emissions
|  |  | Offices | 0 | 15.991 | 15.991 | 15.991 | 3 | 15.991 | 3 | 15.991
|  |  | Schools | 0 | 11.802 | 11.802 | 11.802 | 3 | 11.802 | 3 | 11.802
|  |  | Retailers | 0 | 6.88 | 6.88 | 6.88 | 3 | 6.88 | 3 | 6.88
|  |  | Restaurants | 0 | 6.88 | 6.88 | 6.88 | 3 | 6.88 | 3 | 6.88
|  |  | Halls | 0 | 12.81 | 12.81 | 12.81 | 3 | 12.81 | 3 | 12.81
|  |  | Factories | 0 | 8.65 | 8.65 | 8.65 | 3 | 8.65 | 3 | 8.65
|  |  | Hospitals | 0 | 15.426 | 15.426 | 15.426 | 3 | 15.426 | 3 | 15.426
|  |  | Hotels | 0 | 13.298 | 13.298 | 13.298 | 3 | 13.298 | 3 | 13.298
|  |  | Apartments | 0 | 8.019 | 9.721 | 10.979 | 3 | 8.019 | 3 | 8.019
| 2-2. Subtotal | [7 empty] | 0 |  | 0
3. CO2 Emissions Related to Operation Energy | [8 empty] | kg-CO2/m2-yr |  | kg-CO2/m2-yr |  | N.A.
| 3-1. Building-related Initiatives [2] |  |  | Floor area | Prim. Energy GJ/yr |  | CO2 conversion factor |  | 0 | Ref. bldg. [1] | 0
|  |  |  | m2 | Ref. bldg. [1] | Subj. bldg. [2] | kg-CO2/MJ
|  |  | Building except Apt. area | 0 | 0 | #DIV/0! | #VALUE! |  | 0 |  | 0
|  |  | Apt. Private area (dwelling units total) | 0 | 0 | - | #VALUE! |  | 0 |  | 0
|  |  | Apt. Common area | 0 | 0 | - | #VALUE! |  | 0 |  | 0
| 3-2. Above + Other On-site Measures [3] |  |  | Floor area | Prim. Energy GJ/yr |  | CO2 conversion factor |  | 0
|  |  |  | m2 | Reduced Ene. | Subj. bldg. [3] | kg-CO2/MJ
|  |  | Building except Apt. area | 0 | 0 | #DIV/0! | #VALUE! |  | 0
|  |  | Apt. Private area (dwelling units total) | 0 | 0 | #VALUE! | #VALUE! |  | 0
|  |  | Apt. Common area | 0 | 0 | #VALUE! | #VALUE! |  | 0
売電分
4. Calculation of Life Cycle CO2 (Standard calculation) | [8 empty] | kg-CO2/m2-yr |  | kg-CO2/m2-yr
[9 empty] | CO2 Emissions |  | CO2 Emissions
| Construction | [7 empty] | 0 |  | 0
| Repair, Renewal and Demolition | [7 empty] | 0 |  | 0
| Operation | [7 empty] | 0 |  | 0
| Total | [7 empty] | 0 |  | 0

## Weight
n Weighting coefficients | [11 empty] | Weighting coefficients(default)
[12 empty] | 2 | CASBEE | [14 empty] | 0. 既存 | [15 empty] | １．基本設計 | [15 empty] | 2. Execution and completion stage
|  | After correction |  | Before correction |  | Total (Before correction) |  | Selection of "Excluded" |  | Weighting coefficients (default) |  |  |  |  | Entire Building and Common Properties | [8 empty] | ES/JS/JHS | Residential and Accommodation Sections | [5 empty] | 建物全体・共用部 | [8 empty] | 小中高 | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [8 empty] | 小中高 | 住居・宿泊部 | [5 empty] | Entire Building and Common Properties | [8 empty] | ES/JS/JHS | Residential and Accommodation Sections
|  | Entire Building and Common Properties | Residential and Accomodation sections | Entire Building and Common Properties | Residential and Accomodation sections | Entire Building and Common Properties | Residential and Accomodation sections | Entire Building and Common Properties | Residential and Accomodation sections | Entire Building and Common Properties | Residential and Accomodation sections |  | Item | Name of assessment item | Off | Sch | Rtl | Rst | Hsp | Htl | Apt | Hal | Fct | Sch | Hsp-o | Htl-o | Apt-o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校 | 病院o | ホテルo | 集合住宅o |  | Item | Name of assessment item | Off | Sch | Rtl | Rst | Hsp | Htl | Apt | Hal | Fct | Sch | Hsp-o | Htl-o | Apt-o
| Area ratio | #DIV/0! | #DIV/0! | [10 empty] | Area ratio by building type | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Q | Environmental Quality of the building |  |  |  |  | #DIV/0! | #DIV/0! | [5 empty] | Q | Ratio of Residential & Accommodation Section | [10 empty] | 0 | 0 | 0 | Q |  | 建築物の環境品質 | [13 empty] | Q |  | 建築物の環境品質 | [13 empty] | Q |  | Environmental Quality of the building | bar: Entire Building and Common Properties Off to ES/JS/JHS Sch
Q1 | Indoor Environment | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | Q1 | Q | Indoor Environment | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0 | 0 | 0 | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 |  |  |  | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 |  |  |  | Q1 | Q | Indoor Environment | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4
1 | Noise & Acoustics | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | Q1 | Noise & Acoustics | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15 | 0 | 0 | 0 | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15 |  |  |  | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15 |  |  |  | 1 | Q1 | Noise & Acoustics | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15
1.1 | Noise | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.1 | Q1 1 | Noise | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 1.1 | Q1 1 | 騒音 | 0.4 | 0.4 | 0.8 | 0.4 | 0.4 | 0.8 | 0.8 | 0.8 | 0.5 | 0.4 | 0.5 | 0.4 | 0.4 | 1.1 | Q1 1 | 騒音 | [7 empty] | 0.4 | [5 empty] | 1.1 | Q1 1 | Noise | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5
1.1.1 | Background noise level | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.1.1 | Q1 1.1 | Background noise level | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.1.1 | Q1 1.1 | 室内騒音レベル | 0.4 | 1 | 1 | 1 | 0.4 | 1 | 1 | 1 | 0.4 | 1 | 0.4 | 1 | 1 | 1.1.1 | Q1 1.1 | 室内騒音レベル | [7 empty] | 1 | [5 empty] | 1.1.1 | Q1 1.1 | Background noise level | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
1.1.2 | Equipment noise | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.1.2 | Q1 1.1 | Equipment noise | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.1.2 | Q1 1.1 | 設備騒音対策 | 0.6 |  |  |  | 0.6 |  |  |  | 0.6 |  | 0.6 |  |  | 1.1.2 | Q1 1.1 | 設備騒音対策 | [13 empty] | 1.1.2 | Q1 1.1 | Equipment noise | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
1.2 | Sound Insulation | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.2 | Q1 1 | Sound Insulation | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 1.2 | Q1 1 | 遮音 | 0.4 | 0.4 |  | 0.4 | 0.4 |  |  |  | 0.5 | 0.4 | 0.5 | 0.4 | 0.4 | 1.2 | Q1 1 | 遮音 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1.2 | Q1 1 | Sound Insulation | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5
1.2.1 | Sound Insulation of Openings | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.2.1 | Q1 1.2 | Sound Insulation of Openings | 0.6 | 0.3 | 1 | 0.6 | 0.4 | 1 | 1 | 1 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | 開口部遮音性能 | [13 empty] | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0.6 | 0.4 | 1 | 0.6 | 0.4 | 1 | 1 | 1 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | Sound Insulation of Openings | 0.6 | 0.3 | 1 | 0.6 | 0.4 | 1 | 1 | 1 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3
1.2.2 | Sound Insulation of Partition Walls | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.2.2 | Q1 1.2 | Sound Insulation of Partition Walls | 0.4 | 0.3 | 0 | 0.4 | 0.6 | 0 | 0 | 0 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 1 | 0.4 |  | 1 | 0.4 |  |  |  | 1 | 0.4 | 1 | 0.4 | 0.4 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0.4 | 0.3 |  | 0.4 | 0.6 |  |  |  | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | Sound Insulation of Partition Walls | 0.4 | 0.3 |  | 0.4 | 0.6 |  |  |  | 0.4 | 0.3 | 0.3 | 0.3 | 0.3
1.2.3 | Sound Insulation Performance of Floor Slabs (light-weight impact source) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.2.3 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (light-weight impact source) | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） |  | 0.3 |  |  | 0.6 |  |  |  |  | 0.3 |  | 0.3 | 0.3 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） |  | 0.15 | [7 empty] | 0.15 | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (light-weight impact source) |  | 0.2 | [7 empty] | 0.2 | 0.2 | 0.2 | 0.2
1.2.4 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.2.4 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） |  | 0.3 | [7 empty] | 0.3 |  | 0.3 | 0.3 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） |  | 0.15 | [7 empty] | 0.15 | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) |  | 0.2 | [7 empty] | 0.2 | 0.2 | 0.2 | 0.2
1.3 | Sound Absorption | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.3 | Q1 1 | Sound Absorption | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 1.3 | Q1 1 | 吸音 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 1.3 | Q1 1 | 吸音 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 1.3 | Q1 1 | Sound Absorption | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0
2 | Thermal Comfort | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | Q1 | Thermal Comfort | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35 | 0 | 0 | 0 | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35 |  |  |  | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35 |  |  |  | 2 | Q1 | Thermal Comfort | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35
2.1 | Room Temperature Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.1 | Q1 2 | Room Temperature Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | Room Temperature Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2.1.1 | Room Temperature Setting | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 2.1.1 | Q1 2.1 | Room Temperature Setting | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 2.1.1 | Q1 2.1 | 室温設定 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.3 | 0.3 | 0.3 |  |  |  | 2.1.1 | Q1 2.1 | 室温 | 0.3 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.3 | 0.3 | 0.6 | 0.6 | 0.6 | 0.6 | 2.1.1 | Q1 2.1 | Room Temperature Setting | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5
2.1.2 | Variable Loads and Following-up Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.1.2 | Q1 2.1 | Variable Loads and Following-up Control | 0 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 2.1.2 | Q1 2.1 | 負荷変動・追従制御性 |  | 0.2 | 0.2 | 0.2 |  |  |  | 0.3 |  | 0.2 |  |  |  | 2.1.2 | Q1 2.1 | 負荷変動・追従制御性 | [13 empty] | 2.1.2 | Q1 2.1 | Variable Loads and Following-up Control |  | 0.2 | 0.2 | 0.2 |  |  |  | 0.3 |  | 0.2
2.1.3 | Perimeter Performance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 2.1.3 | Q1 2.1 | Perimeter Performance | 0.2 | 0.2 | 0.1 | 0.1 | 0.2 | 0.2 | 0.3 | 0.1 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.2 | 0.2 | 0.1 | 0.1 | 0.2 | 0.2 | 0.3 | 0.1 | 0.2 | 0.2 | 0.5 | 0.5 | 0.6 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.2 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 2.1.3 | Q1 2.1 | Perimeter Performance | 0.2 | 0.2 | 0.1 | 0.1 | 0.2 | 0.2 | 0.3 | 0.1 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3
2.1.4 | Zoned Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.1.4 | Q1 2.1 | Zoned Control | 0.3 | 0 | 0.2 | 0.2 | 0.3 | 0.3 | 0 | 0.2 | 0.3 | 0 | 0 | 0 | 0 | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.3 |  | 0.2 | 0.2 | 0.3 | 0.3 |  | 0.2 | 0.3 | 0 |  |  |  | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 |  |  |  |  | 2.1.4 | Q1 2.1 | Zoned Control | 0.3 |  | 0.2 | 0.2 | 0.3 | 0.3 |  | 0.2 | 0.3
2.1.5 | Temperature and Humidity Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.1.5 | Q1 2.1 | Temperature and Humidity Control | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0 | 2.1.5 | Q1 2.1 | 温度・湿度制御 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 |  | 2.1.5 | Q1 2.1 | 温度・湿度制御 | [13 empty] | 2.1.5 | Q1 2.1 | Temperature and Humidity Control | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2
2.1.6 | Individual Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.1.6 | Q1 2.1 | Individual Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 2.1.6 | Q1 2.1 | 個別制御 | [9 empty] | 0 | 0.2 | 0.2 | 0.4 | 2.1.6 | Q1 2.1 | 個別制御 | [13 empty] | 2.1.6 | Q1 2.1 | Individual Control | [10 empty] | 0.1 | 0.1 | 0.2
2.1.7 | Allowance for After-hours Air Conditioning | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.1.7 | Q1 2.1 | Allowance for After-hours Air Conditioning | 0.1 | 0.2 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.2 | 0 | 0 | 0 | 2.1.7 | Q1 2.1 | 時間外空調に対する配慮 | 0.1 | 0.2 |  |  | 0.1 | 0.1 |  |  | 0.1 | 0.2 |  |  |  | 2.1.7 | Q1 2.1 | 時間外空調に対する配慮 | [13 empty] | 2.1.7 | Q1 2.1 | Allowance for After-hours Air Conditioning | 0.1 | 0.2 |  |  | 0.1 | 0.1 |  |  | 0.1 | 0.2
2.1.8 | Monitoring Systems | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.1.8 | Q1 2.1 | Monitoring Systems | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.8 | Q1 2.1 | 監視システム |  |  | 0.1 | 0.1 | [5 empty] | 0 |  |  |  | 2.1.8 | Q1 2.1 | 監視システム | [13 empty] | 2.1.8 | Q1 2.1 | Monitoring Systems |  |  | 0.1 | 0.1
2.2 | Humidity Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 2.2 | Q1 2 | Humidity Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | Humidity Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.3 | Type of Air Conditioning System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 1 | #DIV/0! | #DIV/0! | 2.3 | Q1 2 | Type of Air Conditioning System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | Type of Air Conditioning System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
2.3.1 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.3.1 | Q1 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q1 2.3 | 上下温度差 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.3.1 | Q1 2.3 | 上下温度差 | [13 empty] | 2.3.1 | Q1 2.3
2.3.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.3.2 | Q1 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q1 2.3 | 平均気流速度 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.3.2 | Q1 2.3 | 平均気流速度 | [13 empty] | 2.3.2 | Q1 2.3
3 | Lighting & Illumination | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | Q1 | Lighting & Illumination | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0.25 | 0 | 0 | 0 | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0.25 |  |  |  | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 |  |  |  | 3 | Q1 | Lighting & Illumination | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0.25
3.1 | Daylighting | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.1 | Q1 3 | Daylighting | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | Daylighting | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
3.1.1 | Daylight Factor | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 3.1.1 | Q1 3.1 | Daylight Factor | 0.6 | 0.6 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | Daylight Factor | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5
3.1.2 | Openings by Orientation | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 1 | #DIV/0! | #DIV/0! | 3.1.2 | Q1 3.1 | Openings by Orientation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | [12 empty] | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | [12 empty] | 0.3 | 3.1.2 | Q1 3.1 | Openings by Orientation | [12 empty] | 0.3
3.1.3 | Daylight Devices | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 3.1.3 | Q1 3.1 | Daylight Devices | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | Daylight Devices | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.2
3.2 | Anti-glare Measures | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.2 | Q1 3 | Anti-glare Measures | 0.3 | 0.3 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | Anti-glare Measures | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
3.2.1 | Glare from Light Fixtures | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.2.1 | Q1 3.2 | Glare from Light Fixtures | 0.4 | 0.4 | 0 | 0 | 0.4 | 0.4 | 0.4 | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.2.1 | Q1 3.2 | 照明器具のグレア | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 3.2.1 | Q1 3.2 | 照明器具のグレア | [13 empty] | 3.2.1 | Q1 3.2 | Glare from Light Fixtures | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
3.2.2 | Daylight Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 3.2.2 | Q1 3.2 | Daylight Control | 0.6 | 0.6 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.2.2 | Q1 3.2 | 昼光制御 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.4 | 0.6 | 0.6 | 0.6 | 3.2.2 | Q1 3.2 | 昼光制御 | 1 | 1 |  |  | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 3.2.2 | Q1 3.2 | Daylight Control | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
3.2.3 | XXX | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.2.3 | Q1 3.3 | XXX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.3 | Q1 3.3 | 映り込み対策 | [9 empty] | 0.3 |  |  |  | 3.2.3 | Q1 3.3 | 映り込み対策 | [13 empty] | 3.2.3 | Q1 3.3 | XXX
3.3 | Illuminance Level | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 1 | #DIV/0! | #DIV/0! | 3.3 | Q1 3 | Illuminance Level | 0.15 | 0.15 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 |  |  | 0.15 | 0.15 | 0.15 |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 |  |  | 0.15 | 0.15 | 0.15 |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | Illuminance Level | 0.15 | 0.15 |  |  | 0.15 | 0.15 | 0.15 |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
3.3.1 | 照度 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.3.1 | Q1 3.3 | 照度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.1 | Q1 3.3 | 照度 | [13 empty] | 3.3.1 | Q1 3.3 | 照度 | [13 empty] | 3.3.1 | Q1 3.3 | 照度
3.3.2 | 照度均斉度 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.3.2 | Q1 3.3 | 照度均斉度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.2 | Q1 3.3 | 照度均斉度 | [13 empty] | 3.3.2 | Q1 3.3 | 照度均斉度 | [13 empty] | 3.3.2 | Q1 3.3 | 照度均斉度
3.4 | Lighting Controllability | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 3.4 | Q1 3 | Lighting Controllability | 0.25 | 0.25 | 0.5 | 0 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 |  | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 | 0 | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | Lighting Controllability | 0.25 | 0.25 | 0.5 |  | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
4 | Air Quality | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | Q1 | Air Quality | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25 | 0 | 0 | 0 | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25 |  |  |  | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25 |  |  |  | 4 | Q1 | Air Quality | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25
4.1 | Source Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.1 | Q1 4 | Source Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | Source Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625
4.1.1 | Chemical Pollutants | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 4.1.1 | Q1 4.1 | Chemical Pollutants | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1.1 | Q1 4.1 | Chemical Pollutants | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
4.1.2 | Asbestos | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 4.1.2 | Q1 4.1 | Asbestos | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.2 | Q1 4.1 | アスベスト対策 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.2 | Q1 4.1 | アスベスト対策 | [13 empty] | 4.1.2 | Q1 4.1 | Asbestos
4.1.3 | Mites, Mold etc | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 4.1.3 | Q1 4.1 | Mites, Mold etc | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.1.3 | Q1 4.1 | ダニ・カビ等 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.3 | Q1 4.1 | ダニ・カビ等 | [13 empty] | 4.1.3 | Q1 4.1 | Mites, Mold etc | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
4.1.4 | Legionella | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 4.1.4 | Q1 4.1 | Legionella | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.1.4 | Q1 4.1 | レジオネラ対策 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.4 | Q1 4.1 | レジオネラ対策 | [13 empty] | 4.1.4 | Q1 4.1 | Legionella | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
4.2 | Ventilation | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.2 | Q1 4 | Ventilation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | Ventilation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375
4.2.1 | Ventilation Rate | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 4.2.1 | Q1 4.2 | Ventilation Rate | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.2.1 | Q1 4.2 | 換気量 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 |  | 4.2.1 | Q1 4.2 | 換気量 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.1 | Q1 4.2 | Ventilation Rate | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
4.2.2 | Natural Ventilation Performance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 4.2.2 | Q1 4.2 | Natural Ventilation Performance | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.25 | 0.25 | [6 empty] | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333 | 0.33333 | [6 empty] | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.2 | Q1 4.2 | Natural Ventilation Performance | 0.25 | 0.25 | [6 empty] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
4.2.3 | Consideration for Outside Air Intake | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 4.2.3 | Q1 4.2 | Consideration for Outside Air Intake | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 1 | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.3 | Q1 4.2 | Consideration for Outside Air Intake | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
4.2.4 | Air Supply Planning | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 4.2.4 | Q1 4.2 | Air Supply Planning | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.2.4 | Q1 4.2 | 給気計画 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 4.2.4 | Q1 4.2 | 給気計画 | [13 empty] | 4.2.4 | Q1 4.2 | Air Supply Planning | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
4.3 | Operation Plan | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.3 | Q1 4 | Operation Plan | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 |  |  |  | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 |  |  |  | 4.3 | Q1 4 | Operation Plan | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2
4.3.1 | CO2 Monitoring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 4.3.1 | Q1 4.3 | CO2 Monitoring | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.1 | Q1 4.3 | CO2 Monitoring | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5
4.3.2 | Control of Smoking | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 4.3.2 | Q1 4.3 | Control of Smoking | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.2 | Q1 4.3 | Control of Smoking | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  | 0.5 | 0.5 | 0.5
Q2 | Quality of Service | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | Q2 | Q | Quality of Service | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | Q2 | Q | Quality of Service | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
1 | Service Ability | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | Q2 | Service Ability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1 | Q2 | Service Ability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
1.1 | Functionality & Usability | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.1 | Q2 1 | Functionality & Usability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | Functionality & Usability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6
1.1.1 | Provision of Space & Storage | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.1.1 | Q2 1.1 | Provision of Space & Storage | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 1 | 0.5 | 0 | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 | [7 empty] | 0.33333 | 0.5 | 1 | 0.5 |  | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 | [7 empty] | 0.33333 | 0.5 | 1 | 0.5 |  | 1.1.1 | Q2 1.1 | Provision of Space & Storage | 0.33333 | [7 empty] | 0.33333 |  | 1 | 0.5
1.1.2 | Use of Advanced Information System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.1.2 | Q2 1.1 | Use of Advanced Information System | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 | [7 empty] | 0.33333 |  |  | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 | [7 empty] | 0.33333 |  |  | 0.5 | 1 | 1.1.2 | Q2 1.1 | Use of Advanced Information System | 0.33333 | [7 empty] | 0.33333 |  |  | 0.5 | 1
1.1.3 | Barrier-free Planning | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 1.1.3 | Q2 1.1 | Barrier-free Planning | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 1 | 0 | 0 | 0 | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 |  |  |  | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 |  |  |  | 1.1.3 | Q2 1.1 | Barrier-free Planning | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 1
1.2 | Amenity | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.2 | Q2 1 | Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4
1.2.1 | Perceived Spaciousness & Access to View | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 1.2.1 | Q2 1.2 | Perceived Spaciousness & Access to View | 0.33333 | 0.5 | 0.33333 | 0.5 | 0 | 0 | 0 | 0 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | [12 empty] | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | 0.5 | 0.33333 | 0.5 |  |  |  |  | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | Perceived Spaciousness & Access to View | 0.33333 | 0.5 | 0.33333 | 0.5 |  |  |  |  | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5
1.2.2 | Space for Refreshment | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 1.2.2 | Q2 1.2 | Space for Refreshment | 0.33333 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 |  | 0.5 | [10 empty] | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 | 0 | 0.33333 | [5 empty] | 0.33333 | 0 |  |  |  | 1.2.2 | Q2 1.2 | Space for Refreshment | 0.33333 |  | 0.33333 | [5 empty] | 0.33333
1.2.3 | Décor Planning | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.2.3 | Q2 1.2 | Décor Planning | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 1 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.3 | Q2 1.2 | Décor Planning | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5
1.3 | Maintenance Management | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.3 | Q2 1 | Maintenance Management | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.3 | Q2 1 | Maintenance Management | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
1.3.1 | Design Which Considers Maintenance Management | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.3.1 | Q2 1.3 | Design Which Considers Maintenance Management | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 総合的な取組み | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 1.3.1 | Q2 1.3 | Design Which Considers Maintenance Management | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
1.3.2 | Securing Maintenance Management Functions | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 1.3.2 | Q2 1.3 | Securing Maintenance Management Functions | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 清掃管理業務 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 1.3.2 | Q2 1.3 | Securing Maintenance Management Functions | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3.3 | Q2 1.3 | 衛生管理業務 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0
2 | Durability & Reliability | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | Q2 | Durability & Reliability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2 | Q2 | Durability & Reliability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
2.1 | Earthquake Resistance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.1 | Q2 2 | Earthquake Resistance | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.1 | Q2 2 | Earthquake Resistance | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2.1.1 | Earthquake-resistance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.1.1 | Q2 2.1 | Earthquake-resistance | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 2.1.1 | Q2 2.1 | Earthquake-resistance | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
2.1.2 | Seismic Isolation & Vibration Damping Systems | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.1.2 | Q2 2.1 | Seismic Isolation & Vibration Damping Systems | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.1.2 | Q2 2.1 | Seismic Isolation & Vibration Damping Systems | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.2 | Service Life of Components | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.2 | Q2 2 | Service Life of Components | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2.2 | Q2 2 | Service Life of Components | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
2.2.1 | Service Life of Structural Frame Materials | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2.1 | Q2 2.2 | Service Life of Structural Frame Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.1 | Q2 2.2 | Service Life of Structural Frame Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.2.2 | Necessary Refurbishment Interval for Exterior Finishes | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2.2 | Q2 2.2 | Necessary Refurbishment Interval for Exterior Finishes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.2 | Q2 2.2 | Necessary Refurbishment Interval for Exterior Finishes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.2.3 | Necessary Renewal Interval for Main Interior Finishes | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2.3 | Q2 2.2 | Necessary Renewal Interval for Main Interior Finishes | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.3 | Q2 2.2 | Necessary Renewal Interval for Main Interior Finishes | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2.2.4 | Necessary Replacement Interval for Air Conditioning and Ventilation Ducts | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2.4 | Q2 2.2 | Necessary Replacement Interval for Air Conditioning and Ventilation Ducts | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.4 | Q2 2.2 | Necessary Replacement Interval for Air Conditioning and Ventilation Ducts | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2.2.5 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes 99 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2.5 | Q2 2.2 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes 99 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.5 | Q2 2.2 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes 99 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.2.6 | Necessary Renewal Interval for Major Equipment and Services | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2.6 | Q2 2.2 | Necessary Renewal Interval for Major Equipment and Services | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.6 | Q2 2.2 | Necessary Renewal Interval for Major Equipment and Services | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.3 | Appropriate renewal | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.3 | Q2 2 | Appropriate renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q2 2 | 適切な更新 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | Q2 2 | 適切な更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3 | Q2 2 | Appropriate renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.1 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3.1 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.1 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3.2 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.2 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.3 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3.3 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.3 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | Reliability | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.4 | Q2 2 | Reliability | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | Q2 2 | Reliability | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.4.1 | HVAC System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 2.4.1 | Q2 2.4 | HVAC System | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.1 | Q2 2.4 | HVAC System | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.4.2 | Water Supply & Drainage | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 2.4.2 | Q2 2.4 | Water Supply & Drainage | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.2 | Q2 2.4 | Water Supply & Drainage | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.4.3 | Electrical Equipment | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.4.3 | Q2 2.4 | Electrical Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.3 | Q2 2.4 | Electrical Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.4.4 | Support Method of Machines & Ducts | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.4.4 | Q2 2.4 | Support Method of Machines & Ducts | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.4 | Q2 2.4 | Support Method of Machines & Ducts | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.4.5 | Communications & IT Equipment | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.4.5 | Q2 2.4 | Communications & IT Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.5 | Q2 2.4 | Communications & IT Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
0 | 0 |  |  | #DIV/0! | 0 |  |  |  |  | #DIV/0! |  | 0 | Q | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Q | [15 empty] | Q
3 | Flexibility & Adaptability | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | Q2 | Flexibility & Adaptability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q2 | Flexibility & Adaptability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
3.1 | Spatial Margin | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.1 | Q2 3 | Spatial Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | Spatial Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5
3.1.1 | Allowance for Floor-to-floor Height | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 3.1.1 | Q2 3.1 | Allowance for Floor-to-floor Height | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | Allowance for Floor-to-floor Height | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
3.1.2 | Adaptability of Floor Layout | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 3.1.2 | Q2 3.1 | Adaptability of Floor Layout | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | Adaptability of Floor Layout | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
3.2 | Floor Load Margin | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 1 | #DIV/0! | #DIV/0! | 3.2 | Q2 3 | Floor Load Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | Floor Load Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5
3.3 | Adaptability of Facilities | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.3 | Q2 3 | Adaptability of Facilities | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  |  |  | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  |  |  | 3.3 | Q2 3 | Adaptability of Facilities | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4
3.3.1 | Ease of Air Conditioning Duct Renewal | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.1 | Q2 3.3 | Ease of Air Conditioning Duct Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.1 | Q2 3.3 | Ease of Air Conditioning Duct Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
3.3.2 | Ease of Water Supply and Drain Pipe Renewal | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.2 | Q2 3.3 | Ease of Water Supply and Drain Pipe Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.2 | Q2 3.3 | Ease of Water Supply and Drain Pipe Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
3.3.3 | Ease of Electrical Wiring Renewal | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.3 | Q2 3.3 | Ease of Electrical Wiring Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.3 | Q2 3.3 | Ease of Electrical Wiring Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
3.3.4 | Ease of Communications Cable Renewal | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.4 | Q2 3.3 | Ease of Communications Cable Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.4 | Q2 3.3 | Ease of Communications Cable Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
3.3.5 | Ease of Equipment Renewal | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.5 | Q2 3.3 | Ease of Equipment Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.5 | Q2 3.3 | Ease of Equipment Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
3.3.6 | Provision of Backup Space | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.6 | Q2 3.3 | Provision of Backup Space | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.6 | Q2 3.3 | Provision of Backup Space | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Q3 | Outdoor Environment on Site | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | Q3 | Q | Outdoor Environment on Site | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 |  |  |  | Q3 | Q | Outdoor Environment on Site | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3
1 | Preservation & Creation of Biotope | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 1 | Q3 | Preservation & Creation of Biotope | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1 | Q3 | Preservation & Creation of Biotope | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
2 | Townscape & Landscape | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2 | Q3 | Townscape & Landscape | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 2 | Q3 | Townscape & Landscape | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
3 | Local Characteristics & Outdoor Amenity | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | Q3 | Local Characteristics & Outdoor Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q3 | Local Characteristics & Outdoor Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
3.1 | Attention to Local Charcter & Improvement of Comfort | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.1 | Q3 3 | Attention to Local Charcter & Improvement of Comfort | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3.1 | Q3 3 | Attention to Local Charcter & Improvement of Comfort | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
3.2 | Improvement of the Thermal Environment on Site | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.2 | Q3 3 | Improvement of the Thermal Environment on Site | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3.2 | Q3 3 | Improvement of the Thermal Environment on Site | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
0 | Environmental Load Reduction of the building |  |  | #DIV/0! | 0 |  |  |  |  | #DIV/0! |  | 0 | Q | Environmental Load Reduction of the building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q | [15 empty] | Q | Environmental Load Reduction of the building
LR | Environmental Load Reduction of the building |  |  | #VALUE! | #DIV/0! | #VALUE! | #DIV/0! | #VALUE! | 0 | #DIV/0! | #DIV/0! | LR |  | Environmental Load Reduction of the building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | [13 empty] | LR |  | Environmental Load Reduction of the building
LR1 | Energy | #VALUE! | #DIV/0! | #VALUE! | #DIV/0! | #VALUE! | #DIV/0! | #VALUE! | 0 | #DIV/0! | #DIV/0! | LR1 | LR | Energy | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | LR1 | LR | Energy | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
1 | Building Thermal Load | #VALUE! | #DIV/0! | #VALUE! | #DIV/0! |  |  | #VALUE! | 0 | #DIV/0! | #DIV/0! | 1 | LR1 | Building Thermal Load | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 |  |  |  | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 |  |  |  | 1 | LR1 | Building Thermal Load | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2
2 | Natural Energy Utilization | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | LR1 | Natural Energy Utilization | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 | 0 | 0 | 0 | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 |  |  |  | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 |  |  |  | 2 | LR1 | Natural Energy Utilization | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1
0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | 実施・竣工 | [14 empty] | LR | 定量評価 | [14 empty] | LR
0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | LR | 0 | [10 empty] | 0 | 0 | 0 |  | LR | 基本 | [14 empty] | LR | 定性評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | LR |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Entire Building and Common Properties Off to ES/JS/JHS Sch
2.1 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.1 | LR1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | LR1 2 | 自然エネルギーの直接利用 | [13 empty] | 2.1 | LR1 2 | 自然エネルギーの直接利用 | [13 empty] | 2.1 | LR1 2
2.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 2.2 | LR1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | LR1 2 | 自然エネルギーの変換利用 | [13 empty] | 2.2 | LR1 2 | 自然エネルギーの変換利用 | [13 empty] | 2.2 | LR1 2
3 | Efficiency in Building Service System | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 3 | LR1 | Efficiency in Building Service System | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 | 0 | 0 | 0 | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 |  |  |  | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 |  |  |  | 3 | LR1 | Efficiency in Building Service System | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5
3a.3b | Other than apartment (3a.3b) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3a.3b | LR1 3 | Other than apartment (3a.3b) | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 3a | LR1 3 | ERRによる評価 | [13 empty] | 3a | LR1 3 | 非住宅部分 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 3a.3b | LR1 3 | Other than apartment (3a.3b) | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1
3b.c | Apartment (3c) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 3b.c | LR1 3 | Apartment (3c) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3b | LR1 3 | ERR以外による評価 | [13 empty] | 3b | LR1 3 | 集合住宅の評価 | [6 empty] | 1 | [6 empty] | 3b.c | LR1 3 | Apartment (3c) | [6 empty] | 1
3.1 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.1 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | LR1 3b | 空調設備 | [9 empty] | 0.65 |  |  |  | 3.1 | LR1 3b | 空調設備 | [9 empty] | 0.65 |  |  |  | 3.1 | LR1 3b | [14 empty] | 122
3.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.2 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | LR1 3b | 換気設備 | [9 empty] | 0.1 |  |  |  | 3.2 | LR1 3b | 換気設備 | [9 empty] | 0.1 |  |  |  | 3.2 | LR1 3b | [14 empty] | 123
3.3 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.3 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | LR1 3b | 照明設備 | [9 empty] | 0.2 |  |  |  | 3.3 | LR1 3b | 照明設備 | [9 empty] | 0.2 |  |  |  | 3.3 | LR1 3b | [14 empty] | 124
3.4 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.4 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | LR1 3b | 給湯設備 | [9 empty] | 0.05 |  |  |  | 3.4 | LR1 3b | 給湯設備 | [9 empty] | 0.05 |  |  |  | 3.4 | LR1 3b | [14 empty] | 125
3.5 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 3.5 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | LR1 3b | 昇降機設備 | [13 empty] | 3.5 | LR1 3b | 昇降機設備 | [13 empty] | 3.5 | LR1 3b | [14 empty] | 126
0 | 0 |  |  | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | [15 empty] | LR | [15 empty] | LR | [14 empty] | 127
4 | Efficient Operation | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | LR1 | Efficient Operation | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0 | 0 | 0 | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 |  |  |  | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 |  |  |  | 4 | LR1 | Efficient Operation | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 |  |  |  | 128
4.1 | Other than apartments | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.1 | LR1 4 | Other than apartments | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 4.1 | LR1 4 | Other than apartments | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 129
4.1.1 | Monitoring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 4.1.1 | LR1 4.1 | Monitoring | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.1 | LR1 4.1 | Monitoring | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5
4.1.2 | Operation & Management System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 4.1.2 | LR1 4.1 | Operation & Management System | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.2 | LR1 4.1 | Operation & Management System | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5
4.2 | Apartments | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.2 | LR1 4 | Apartments | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | LR1 4 | 住宅の評価 | [6 empty] | 1 | [6 empty] | 4.2 | LR1 4 | 住宅の評価 | [6 empty] | 1 | [6 empty] | 4.2 | LR1 4 | Apartments | [6 empty] | 1
4.2.1 | Monitoring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 4.2.1 | LR1 4.2 | Monitoring | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.1 | LR1 4.2 | 住まい方の提示 | [6 empty] | 0.5 | [6 empty] | 4.2.1 | LR1 4.2 | モニタリング | [6 empty] | 0.5 | [6 empty] | 4.2.1 | LR1 4.2 | Monitoring | [6 empty] | 0.5
4.2.2 | Operation & Management System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 4.2.2 | LR1 4.2 | Operation & Management System | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.2 | LR1 4.2 | エネルギーの管理と制御 | [6 empty] | 0.5 | [6 empty] | 4.2.2 | LR1 4.2 | 運用管理体制 | [6 empty] | 0.5 | [6 empty] | 4.2.2 | LR1 4.2 | Operation & Management System | [6 empty] | 0.5
LR2 | Resources & Materials | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | LR2 | LR | Resources & Materials | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR2 | LR | Resources & Materials | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
1 | Water Resources | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | LR2 | Water Resources | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR2 | Water Resources | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
1.1 | Water Saving | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 1.1 | LR2 1 | Water Saving | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1.1 | LR2 1 | Water Saving | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
1.2 | Rainwater & Gray Water | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.2 | LR2 1 | Rainwater & Gray Water | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 1.2 | LR2 1 | Rainwater & Gray Water | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
1.2.1 | Rainwater Use System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 1.2.1 | LR2 1.2 | Rainwater Use System | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 1.2.1 | LR2 1.2 | Rainwater Use System | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
1.2.2 | Gray Water Reuse System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 1.2.2 | LR2 1.2 | Gray Water Reuse System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.2.2 | LR2 1.2 | Gray Water Reuse System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
2 | Reducing Usage of Non-renewable Resources | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | LR2 | Reducing Usage of Non-renewable Resources | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 2 | LR2 | Reducing Usage of Non-renewable Resources | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
2.1 | Reducing Usage of Materials | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.1 | LR2 2 | Reducing Usage of Materials | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.1 | LR2 2 | Reducing Usage of Materials | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2.2 | Continuing Use of Existing Building Skeleton etc | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2 | LR2 2 | Continuing Use of Existing Building Skeleton etc | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | LR2 2 | Continuing Use of Existing Building Skeleton etc | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.3 | Use of Recycled Materials as Structural Frame Materials | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3 | LR2 2 | Use of Recycled Materials as Structural Frame Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.3 | LR2 2 | Use of Recycled Materials as Structural Frame Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.4 | Use of Recycled Materials as Non-structural Materials | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.4 | LR2 2 | Use of Recycled Materials as Non-structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | LR2 2 | Use of Recycled Materials as Non-structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2.5 | Timber from Sustainable Forestry | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.5 | LR2 2 | Timber from Sustainable Forestry | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.5 | LR2 2 | Timber from Sustainable Forestry | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
2.6 | Reusability of Components and Materials | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.6 | LR2 2 | Reusability of Components and Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.6 | LR2 2 | Reusability of Components and Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
3 | Avoiding the Use of Materials with Pollutant Content | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | LR2 | Avoiding the Use of Materials with Pollutant Content | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3 | LR2 | Avoiding the Use of Materials with Pollutant Content | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
3.1 | Use of Materials without Harmful Substances | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.1 | LR2 3 | Use of Materials without Harmful Substances | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.1 | LR2 3 | Use of Materials without Harmful Substances | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
3.2 | Avoidance of CFCs and Halons | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.2 | LR2 3 | Avoidance of CFCs and Halons | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.2 | LR2 3 | Avoidance of CFCs and Halons | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
3.2.1 | Fire Retardant | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.2.1 | LR2 3.2 | Fire Retardant | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.1 | LR2 3.2 | Fire Retardant | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
3.2.2 | Insulation Materials | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.2.2 | LR2 3.2 | Insulation Materials | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.2 | LR2 3.2 | Insulation Materials | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
3.2.3 | Refrigerants | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.2.3 | LR2 3.2 | Refrigerants | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.3 | LR2 3.2 | Refrigerants | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
LR3 | Off-site Environment | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | LR3 | LR | Off-site Environment | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR3 | LR | Off-site Environment | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
1 | Consideration of Global Warming | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | 0 | #DIV/0! | #DIV/0! | 1 | LR3 | Consideration of Global Warming | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 1 | LR3 | Consideration of Global Warming | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
2 | Consideration of Local Environment | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | LR3 | Consideration of Local Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2 | LR3 | Consideration of Local Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
2.1 | Air Pollution | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.1 | LR3 2 | Air Pollution | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.1 | LR3 2 | Air Pollution | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
2.2 | Heat Island Effect | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.2 | LR3 2 | Heat Island Effect | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.2 | LR3 2 | Heat Island Effect | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2.3 | Load on Local Infrastructure | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.3 | LR3 2 | Load on Local Infrastructure | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | LR3 2 | Load on Local Infrastructure | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
2.3.1 | Reduction of Rainwater Discharge Loads | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3.1 | LR3 2.3 | Reduction of Rainwater Discharge Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.1 | LR3 2.3 | Reduction of Rainwater Discharge Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
2.3.2 | Sewage Load Suppression | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3.2 | LR3 2.3 | Sewage Load Suppression | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.2 | LR3 2.3 | Sewage Load Suppression | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
2.3.3 | Traffic Load Control | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3.3 | LR3 2.3 | Traffic Load Control | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.3 | LR3 2.3 | Traffic Load Control | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
2.3.4 | Waste Treatment Loads | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 2.3.4 | LR3 2.3 | Waste Treatment Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.4 | LR3 2.3 | Waste Treatment Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
3 | Consideration of Surrounding Environment | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | LR3 | Consideration of Surrounding Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3 | LR3 | Consideration of Surrounding Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
3.1 | Noise, Vibration & Odor | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.1 | LR3 3 | Noise, Vibration & Odor | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.1 | LR3 3 | Noise, Vibration & Odor | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
3.1.1 | Noise | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.1.1 | LR3 3.1 | Noise | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.1 | LR3 3.1 | Noise | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
3.1.2 | Vibration | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.1.2 | LR3 3.1 | Vibration | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.2 | LR3 3.1 | Vibration | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
3.1.3 | Odor | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.1.3 | LR3 3.1 | Odor | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.3 | LR3 3.1 | Odor | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333
3.2 | Wind Damage & Sunlight Obstruction | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.2 | LR3 3 | Wind Damage & Sunlight Obstruction | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.2 | LR3 3 | 風害、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.2 | LR3 3 | 風害・砂塵、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.2 | LR3 3 | Wind Damage & Sunlight Obstruction | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
3.2.1 | Restriction of Wind Damage | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.2.1 | LR3 3.2 | Restriction of Wind Damage | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0 | 0 | 0 | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 |  |  |  | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 |  |  |  | 3.2.1 | LR3 3.2 | Restriction of Wind Damage | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6
3.2.2 | Restriction of Sand and Dust | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.2.2 | LR3 3.2 | Restriction of Sand and Dust | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2.3 | LR3 3.3 | 砂塵の抑制 | [9 empty] | 0.2 |  |  |  | 3.2.2 | LR3 3.2 | 砂塵の抑制 | [9 empty] | 0.2 |  |  |  | 3.2.2 | LR3 3.2 | Restriction of Sand and Dust | [9 empty] | 0.2
3.2.3 | Restriction of sunlight obstruction | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.2.3 | LR3 3.2 | Restriction of sunlight obstruction | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0 | 0 | 0 | 3.2.2 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 |  |  |  | 3.2.3 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 |  |  |  | 3.2.3 | LR3 3.2 | Restriction of sunlight obstruction | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2
3.3 | Light Pollution | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.3 | LR3 3 | Light Pollution | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3 | LR3 3 | Light Pollution | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
3.3.1 | Outdoor Illumination and Light that Spills from Interiors | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.1 | LR3 3.3 | Outdoor Illumination and Light that Spills from Interiors | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.3.1 | LR3 3.3 | Outdoor Illumination and Light that Spills from Interiors | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
3.3.2 | Measures for Reflected Solar Glare from Building Walls | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 1 | 0 | #DIV/0! | #DIV/0! | 3.3.2 | LR3 3.3 | Measures for Reflected Solar Glare from Building Walls | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.3.2 | LR3 3.3 | Measures for Reflected Solar Glare from Building Walls | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3

## Std.
n LCCO2 Calculation Conditions Sheet (Standard Calculation) |  |  | n Building Name | XXX Building
CASBEE-BD_NCe_2014(v.2.1)
Items |  | Reference Values (Reference Building) | Subject | Note
Building Overview | Building type
| Gross floor area | 0 | 0
| Structure | S | S
Life Cycle | Estimated service life
| CO2 emissions | 0 | 0 | kg-CO2/yr-m2
Construction Stage | Embodied CO2 calculation method | Japan's average CO2 emissions based on 2005 I-O table analysis by the Architectural Institute of Japan | Estimated by subtracting CO2 reduction due to recycled material use from the
| Reference for CO2 |  | reference value
| Boundary | CO2 emissions based on the analysis of the 2005 I-O Table by the Architectural | See reference method
Representative main material amounts
| Regular concrete | 0 | 0 | m3/m2
| Blast furnace cement concrete | 0 | 0 | m3/m2
| Steel frame | 0 | 0 | t/m2
| 鉄骨 (電炉） | 0 | 0 | t/m2
| Steel reinforced | 0 | 0 | t/m2
| Timber | 0 | 0 | t/m2
| XXX | XXXXX | XXXXX | kg/m2
Representative material environmental load
| Regular concrete | 266.71 | 266.71 | kg-CO2/m3
| Blast furnace cement concrete | 216.57 | 216.57 | kg-CO2/m3
| Steel frame | 1.28 | 1.28 | kg-CO2/kg
| Steel frame (electric furnace) |  | 0 | kg-CO2/ｔ
| Steel reinforced | 0.51 | 0.51 | kg-CO2/kg
| Cement formwork | 4.75 | 4.75 | kg-CO2/m2
| XXX | XXXXX | XXXXX | kg-CO2/kg
Main recycled materials and usage
| Blast furnace cement (structural use) | 0% | 0%
| Existing frame materials (structural use) | 0% | 0%
| Electric furnace steel (reinforcement) | 0% | 0%
| Electric furnace steel (steel materials) | 0% | 0%
| CO2 emissions | 0 | 0 | kg-CO2/yr-m2
Maintenance/ | Upgrade period (year)
Upgrade/ | Exterior | 25 | 25
屋根
Demolition Stage | Interior | 18 | 18
| Service system | 15 | 15
Average maintenance rate (%/year)
| Exterior | 1% | 1%
| Interior | 1% | 1%
| Service system | 2% | 2%
| Calculation method for demolition-related CO2 emissions | Estimated assuming demolition materials of 2,000 kg/m2 and road transport distance of 30 km | See reference method
CO2 emissions
| [1] Reference value/ [2] Building-related initiatives | 0 | 0 | kg-CO2/yr-m2
| [3] Above + other on-site initiatives | － | 0 | kg-CO2/yr-m2
Operation Stage |  |  |  | kg-CO2/yr-m2
kg-CO2/yr-m2
|  |  | #VALUE! | kg-CO2/yr-m2
|  | その他再生可能エネルギー | － | kg-CO2/yr-m2
| [4] Above + other off-site measures | － | 0 | kg-CO2/yr-m2
| Reference | (a) Carbon offsetting with renewable energy certificates | －
|  | (b) Carbon offsetting with green heat certificate | －
|  | (c) Other carbon credit | －
|  | (d) Difference between actual and adjusted emissions (obtained from the adjusted emissions coefficient) | －
－
| Calculation method for energy consumption | Average primary energy consumptions based on statistical value | Estimated based on energy conservation achieved with LR1-related measures
| Primary energy consumption | 0 | #DIV/0! | GJ/year
CO2 emissions coefficient for energy
| Primary energy Non-residential buildings | #VALUE! | #VALUE! | kg-CO2/MJ
| Primary energy Residential buildings (Private areas) | #VALUE! | #VALUE! | kg-CO2/MJ
| Electricity | #VALUE! | #VALUE! | kg-CO2/ｋWh
| Gas | 0.0498 | 0.0498 | kg-CO2/MJ
| Other fuels （ ） | XXXXX | XXXXX | kg-CO2/MJ
Potable water
Other

## Individual
n LCCO2 Calculation Conditions Sheet (Individual Calculation) |  |  | n Building Name | XXX Building
CASBEE-BD_NCe_2014(v.2.1)
Items |  | Reference Values (Reference Building) | Subject | Note
Building Overview | Building type
| Gross floor area | 0 | 0
| Structure | S | S
Life Cycle | Estimated service life
| CO2 emissions | 30 | 30 | kg-CO2/yr-m2
Construction Stage | Embodied CO2 calculation method
Reference for CO2
Boundary
Representative main material amounts
| Regular concrete | XXXXX | XXXXX | m3/m2
| Blast furnace cement concrete | XXXXX | XXXXX | m3/m2
| Steel frame | XXXXX | XXXXX | t/m2
| 鉄骨 (電炉） | XXXXX | XXXXX | t/m2
| Steel reinforced | XXXXX | XXXXX | t/m2
| Timber | XXXXX | XXXXX | t/m2
| XXX | XXXXX | XXXXX | kg/m2
Representative material environmental load
| Regular concrete | XXXXX | XXXXX | kg-CO2/m3
| Blast furnace cement concrete | XXXXX | XXXXX | kg-CO2/m3
| Steel frame | XXXXX | XXXXX | kg-CO2/kg
| Steel frame (electric furnace) | XXXXX | XXXXX | kg-CO2/kg
| Steel reinforced | XXXXX | XXXXX | kg-CO2/kg
| Cement formwork | XXXXX | XXXXX | kg-CO2/m2
| XXX | XXXXX | XXXXX | kg-CO2/kg
Main recycled materials and usage
| Blast furnace cement (structural use) | XXXXX | XXXXX
| Existing frame materials (structural use) | XXXXX | XXXXX
| Electric furnace steel (reinforcement) | XXXXX | XXXXX
| Electric furnace steel (steel materials) | XXXXX | XXXXX
| CO2 emissions | 10 | 10 | kg-CO2/yr-m2
Maintenance/ | Upgrade period (year)
Upgrade/ | Exterior
0 | 屋根
Demolition Stage | Interior
Service system
Average maintenance rate (%/year)
Exterior
Interior
Service system
Calculation method for demolition-related CO2 emissions
CO2 emissions
| [1] Reference value/ [2] Building-related initiatives | 30 | 20 | kg-CO2/yr-m2
| [3] Above + other on-site initiatives | － | -15 | kg-CO2/yr-m2
Operation Stage |  | 0 |  | kg-CO2/yr-m2
|  | 0 |  | kg-CO2/yr-m2
|  | 0 |  | kg-CO2/yr-m2
|  | その他再生可能エネルギー |  | kg-CO2/yr-m2
| [4] Above + other off-site measures | － | -25 | kg-CO2/yr-m2
| Reference | (a) Carbon offsetting with renewable energy certificates
(b) Carbon offsetting with green heat certificate
(c) Other carbon credit
(d) Difference between actual and adjusted emissions (obtained from the adjusted emissions coefficient)
| 0 |  | #VALUE! | kg-CO2/年㎡
| Calculation method for energy consumption | XXXXX | XXXXX
| Primary energy consumption | XXXXX | XXXXX | MJ/yr-m2
CO2 emissions coefficient for energy
| Primary energy Non-residential buildings | XXXXX | XXXXX | kg-CO2/MJ
| Primary energy Residential buildings (Private areas) | XXXXX | XXXXX | kg-CO2/MJ
| Electricity | XXXXX | XXXXX | kg-CO2/ｋWh
| Gas | XXXXX | XXXXX | kg-CO2/MJ
| Other fuels （ ） | XXXXX | XXXXX | kg-CO2/MJ
Potable water
Other
<Reference> Values available for individual calculation
Reduction in CO2 emissions with use of solar power (Apply only when the amount of power generated is equivalent to 3. On-site efforts, and when the emission coefficient for electricity is used for the reduced amount.)
| Solar-generated power | Total | 0 | kWh/yr
Operation |  | In-house consumption | 0 | kWh/yr
Stage |  | Excess power sold | 0 | kWh/yr
| Reduction in CO2 emission | Total (1) | #VALUE! | kg-CO2/yr-m2
|  | In-house consumption | #VALUE! | kg-CO2/yr-m2
|  | Excess power sold | #VALUE! | kg-CO2/yr-m2
| 算定に用いた排出係数 | 自家消費分 | #VALUE! | kg-CO2/kWh
|  | 余剰売電分 | #VALUE! | kg-CO2/kWh
|  | 備考 | 実排出係数の場合
Difference over emission value (using adjusted coefficient)
| Electricity consumption of the subject building [3]. |  | #DIV/0! | kWh/yr
| Emission coefficient | Actual emissions coefficient | #VALUE! | kg-CO2/kWh
|  | Adjusted emission coefficient | #VALUE! | kg-CO2/kWh
| Difference over actual emission | Entire building | #VALUE! | kg-CO2/yr
|  | Per gross floor area (2) | #VALUE! | kg-CO2/yr-m2
Note on D48: 下表＜参考＞ [1]の数値を利用できる。
Note on D56: Table below, <Reference> Values in (2) can be used.

## CO2data
n CO2 Data base
| a. CO2 Emissions Related to Construction | [5 empty] | Q2/2.2.1 Service Life of Structural Frame Materials
|  | kg-CO2/m2-yr |  |  |  |  | S | ,Wood |  | RC |  |  | SRC
| Building Type | [5 empty] | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5
[5 empty] | 1 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Office |  |  |  | 10 |  | 14.005 | 14.005 | 14.005 | 13.23 | 13.23 | 13.23 | 13.998 | 13.998 | 13.998
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 11 |  | 6.452 | 6.452 | 6.452 | 6.601 | 6.601 | 6.601 | 6.515 | 6.515 | 6.515
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 12 |  | 13.42 | 13.42 | 13.42 | 12.416 | 12.416 | 12.416 | 13.272 | 13.272 | 13.272
|  | LR2/2.2 削減分 |  |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 15 |  | 14.005 | 14.005 | 14.005 | 13.23 | 13.23 | 13.23 | 13.998 | 13.998 | 13.998
| School |  |  |  | 20 |  | 10.473 | 10.473 | 10.473 | 11.763 | 11.763 | 11.763 | 14.002 | 14.002 | 14.002
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 21 |  | 5.228 | 5.228 | 5.228 | 5.369 | 5.369 | 5.369 | 5.278 | 5.278 | 5.278
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 22 |  | 10.11 | 10.11 | 10.11 | 10.846 | 10.846 | 10.846 | 13.005 | 13.005 | 13.005
|  | LR2/2.2 削減分 |  |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 25 |  | 10.473 | 10.473 | 10.473 | 11.763 | 11.763 | 11.763 | 14.002 | 14.002 | 14.002
| Retailers |  |  |  | 30 |  | 16.572 | 16.572 | 16.572 | 22.386 | 22.386 | 22.386 | 16.961 | 16.961 | 16.961
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 31 |  | 8.404 | 8.404 | 8.404 | 8.599 | 8.599 | 8.599 | 8.485 | 8.485 | 8.485
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 32 |  | 15.867 | 15.867 | 15.867 | 20.512 | 20.512 | 20.512 | 16.322 | 16.322 | 16.322
|  | LR2/2.2 削減分 |  |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 35 |  | 16.572 | 16.572 | 16.572 | 22.386 | 22.386 | 22.386 | 16.961 | 16.961 | 16.961
| Restaurants |  |  |  | 40 |  | 16.572 | 16.572 | 16.572 | 22.386 | 22.386 | 22.386 | 16.961 | 16.961 | 16.961
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 41 |  | 8.404 | 8.404 | 8.404 | 8.599 | 8.599 | 8.599 | 8.485 | 8.485 | 8.485
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 42 |  | 15.867 | 15.867 | 15.867 | 20.512 | 20.512 | 20.512 | 16.322 | 16.322 | 16.322
|  | LR2/2.2 削減分 |  |  | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 45 |  | 16.572 | 16.572 | 16.572 | 22.386 | 22.386 | 22.386 | 16.961 | 16.961 | 16.961
| Halls |  |  |  | 50 |  | 11.535 | 11.535 | 11.535 | 12.471 | 12.471 | 12.471 | 13.079 | 13.079 | 13.079
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 51 |  | 5.452 | 5.452 | 5.452 | 5.578 | 5.578 | 5.578 | 5.504 | 5.504 | 5.504
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 52 |  | 11.178 | 11.178 | 11.178 | 11.534 | 11.534 | 11.534 | 12.182 | 12.182 | 12.182
|  | LR2/2.2 削減分 |  |  | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 55 |  | 11.535 | 11.535 | 11.535 | 12.471 | 12.471 | 12.471 | 13.079 | 13.079 | 13.079
| Factories |  |  |  | 60 |  | 19.562 | 19.562 | 19.562 | 22.5 | 22.5 | 22.5 | 23.65 | 23.65 | 23.65
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 61 |  | 9.985 | 9.985 | 9.985 | 10.302 | 10.302 | 10.302 | 9.97 | 9.97 | 9.97
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 62 |  | 18.811 | 18.811 | 18.811 | 20.812 | 20.812 | 20.812 | 22.232 | 22.232 | 22.232
|  | LR2/2.2 削減分 |  |  | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 65 |  | 19.562 | 19.562 | 19.562 | 22.5 | 22.5 | 22.5 | 23.65 | 23.65 | 23.65
| Hospitals |  |  |  | 70 |  | 10.405 | 10.405 | 10.405 | 12.261 | 12.261 | 12.261 | 13.704 | 13.704 | 13.704
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 71 |  | 6.299 | 6.299 | 6.299 | 6.445 | 6.445 | 6.445 | 6.36 | 6.36 | 6.36
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 72 |  | 10.078 | 10.078 | 10.078 | 11.452 | 11.452 | 11.452 | 12.858 | 12.858 | 12.858
|  | LR2/2.2 削減分 |  |  | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 75 |  | 10.405 | 10.405 | 10.405 | 12.261 | 12.261 | 12.261 | 13.704 | 13.704 | 13.704
| Hotels |  |  |  | 80 |  | 11.119 | 11.119 | 11.119 | 12.77 | 12.77 | 12.77 | 13.53 | 13.53 | 13.53
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 81 |  | 5.557 | 5.557 | 5.557 | 5.686 | 5.686 | 5.686 | 5.61 | 5.61 | 5.61
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 82 |  | 10.67 | 10.67 | 10.67 | 11.716 | 11.716 | 11.716 | 12.681 | 12.681 | 12.681
|  | LR2/2.2 削減分 |  |  | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 85 |  | 11.119 | 11.119 | 11.119 | 12.77 | 12.77 | 12.77 | 13.53 | 13.53 | 13.53
| Apartments |  |  |  | 90 |  | 15.641 | 7.821 | 5.214 | 19.62 | 9.808 | 6.539 | 22.378 | 11.188 | 7.459
|  | LR2/2.2 Existing Building Skeleton etc. |  | 100% | 91 |  | 9.094 | 4.546 | 3.031 | 8.833 | 4.416 | 2.943 | 8.747 | 4.373 | 2.915
|  | LR2/2.3 Recycled Materials as Structural Frame Materials (Blast furnace cement (concrete)) |  | 100% | 92 |  | 14.974 | 7.488 | 4.991 | 18.149 | 9.073 | 6.049 | 20.89 | 10.444 | 6.962
|  |  | LR2/2.2 削減分 |  | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | LR2/2.3 削減分 |  | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 合計 |  | 95 |  | 15.641 | 7.821 | 5.214 | 19.62 | 9.808 | 6.539 | 22.378 | 11.188 | 7.459
| b. CO2 Emissions Related to Repair, Renewal and Demolition | [5 empty] | Level 3 3: Q2/2.2.1 Service Life of Structural Frame Materials
|  | kg-CO2/m2-yr |  |  |  |  | Level 3 3: S; Level 4 4: ,Wood; Level 3 6: RC; Level 3 9: SRC
| Building Type | [5 empty] | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5
| Office |  |  |  | 1 |  | 15.991 | 15.991 | 15.991 | 16.456 | 16.456 | 16.456 | 16.21 | 16.21 | 16.21
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 15.991 | 15.991 | 15.991 | 16.456 | 16.456 | 16.456 | 16.21 | 16.21 | 16.21
| School |  |  |  | 2 |  | 11.802 | 11.802 | 11.802 | 12.424 | 12.424 | 12.424 | 12.306 | 12.306 | 12.306
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 11.802 | 11.802 | 11.802 | 12.424 | 12.424 | 12.424 | 12.306 | 12.306 | 12.306
| Retailers |  |  |  | 3 |  | 6.88 | 6.88 | 6.88 | 7.738 | 7.738 | 7.738 | 6.91 | 6.91 | 6.91
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 6.88 | 6.88 | 6.88 | 13.194 | 13.194 | 13.194 | 6.91 | 6.91 | 6.91
| Restaurants |  |  |  | 4 |  | 6.88 | 6.88 | 6.88 | 7.738 | 7.738 | 7.738 | 6.91 | 6.91 | 6.91
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 6.88 | 6.88 | 6.88 | 7.738 | 7.738 | 7.738 | 6.91 | 6.91 | 6.91
| Halls |  |  |  | 5 |  | 12.81 | 12.81 | 12.81 | 13.426 | 13.426 | 13.426 | 13.251 | 13.251 | 13.251
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 12.81 | 12.81 | 12.81 | 13.426 | 13.426 | 13.426 | 13.251 | 13.251 | 13.251
| Factories |  |  |  | 6 |  | 8.65 | 8.65 | 8.65 | 9.422 | 9.422 | 9.422 | 9.061 | 9.061 | 9.061
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 8.65 | 8.65 | 8.65 | 9.422 | 9.422 | 9.422 | 9.061 | 9.061 | 9.061
| Hospitals |  |  |  | 7 |  | 15.426 | 15.426 | 15.426 | 16.054 | 16.054 | 16.054 | 15.894 | 15.894 | 15.894
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 15.426 | 15.426 | 15.426 | 16.054 | 16.054 | 16.054 | 15.894 | 15.894 | 15.894
| Hotels |  |  |  | 8 |  | 13.298 | 13.298 | 13.298 | 13.942 | 13.942 | 13.942 | 13.671 | 13.671 | 13.671
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 13.298 | 13.298 | 13.298 | 13.942 | 13.942 | 13.942 | 13.671 | 13.671 | 13.671
| Apartments |  |  |  | 9 |  | 8.019 | 9.721 | 10.979 | 8.371 | 9.735 | 10.863 | 8.364 | 9.68 | 10.783
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 8.019 | 9.721 | 10.979 | 8.371 | 9.735 | 10.863 | 8.364 | 9.68 | 10.783
c. CO2 Emissions Related to Operation Energy
Emissions coefficient
|  | Electricity (Actual value) |  | kg-CO2/kWh |  |  | Level 3: #VALUE!; Level 4: Provide evidence; Level 4: (Adjusted emission coefficient; Level 3: #VALUE!; Level 4: kg-CO2/kWh)
|  |  |  | kg-CO2/MJ |  |  | Level 3: #VALUE!; Level 4: 9.76; Level 5: MJ/kWh conversion （all day average in 2013 by Energy saving law) |  |  | #VALUE!
|  | Town gas |  | kg-CO2/MJ |  |  | Level 3: 0.0498
|  | DHC |  | kg-CO2/MJ |  |  | Level 3: 0.057
|  | Kerosene |  | kg-CO2/MJ |  |  | Level 3: 0.0678
|  | Type A heavy oil |  | kg-CO2/MJ |  |  | Level 3: 0.0693
|  | Other |  | kg-CO2/MJ |  |  | Level 3: 0.06855; Level 4: (Average of Kerosene&Type A heavy oil)
|  | LPG |  | kg-CO2/MJ |  |  | Level 3: 0.059
Published Actual/adjusted CO2 emission coefficients per PPS in 2012
|  | Name of company |  |  |  |  | Level 3: Actual emissions coefficient/ Alternative coefficient; Level 5: Adjusted emission coefficient
|  | Hokkaido Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000688; Level 4: (t-CO2/kWh); Level 5: 0.00068; Level 3: (t-CO2/kWh)
|  | Tohoku Electric Power Co., Inc. |  |  |  |  | Level 3: 0.0006; Level 5: 0.00056
|  | Tokyo Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000525; Level 5: 0.000406
|  | Chubu Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000516; Level 5: 0.000373
|  | Hokuriku Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000663; Level 5: 0.000494
|  | Kansai Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000514; Level 5: 0.000475
|  | Chugoku Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000738; Level 5: 0.000672
|  | Shikoku Electric Power Co., Inc. |  |  |  |  | Level 3: 0.0007; Level 5: 0.000656
|  | Kyushu Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000612; Level 5: 0.000599
|  | Okinawa Electric Power Co., Inc. |  |  |  |  | Level 3: 0.000903; Level 5: 0.000692
|  | eREX Co., Ltd. |  |  |  |  | Level 3: 0.000603; Level 5: 0.000428
|  | Idemitsu Green Power Co., Ltd. |  |  |  |  | Level 3: 8.6e-05; Level 5: 0.000106
|  | Itochu Enex Co., Ltd. |  |  |  |  | Level 3: 0.000676; Level 5: 0.000293
|  | Eneserve Corp. |  |  |  |  | Level 3: 0.000616; Level 5: 0.000482
|  | Ebara Environmental Plant Co., Ltd. |  |  |  |  | Level 3: 0.000456; Level 5: 0.000456
|  | Oji Paper Co., Ltd. |  |  |  |  | Level 3: 0.000475; Level 5: 0.000471
|  | ORIX Corp. |  |  |  |  | Level 3: 0.000762; Level 5: 0.000757
|  | e-sell Co.,Ltd. |  |  |  |  | Level 3: 0; Level 5: 0
|  | Ennet Corp. |  |  |  |  | Level 3: 0.000429; Level 5: 0.000427
|  | F-Power Co., Ltd. |  |  |  |  | Level 3: 0.000525; Level 5: 0.000445
|  | G-Power Co., Ltd. |  |  |  |  | Level 3: 0.000441; Level 5: 0
|  | Nihon Ceremony Corp. |  |  |  |  | Level 3: 0.000797; Level 5: 0.000789
|  | Summit Energy Corp. |  |  |  |  | Level 3: 0.000438; Level 5: 0.000259
|  | JX Nippon Oil & Energy Corp. |  |  |  |  | Level 3: 0.000367; Level 5: 0.000364
|  | J JEN Holdings Co., Ltd. |  |  |  |  | Level 3: 0.000494; Level 5: 0.00049
|  | Shigakogen Resort Kaihatsu Corp. |  |  |  |  | Level 3: 0.000312; Level 5: 0.000309
|  | Showa Shell Sekiyu K.K. |  |  |  |  | Level 3: 0.000367; Level 5: 0.000364
|  | Nippon Steel & Sumikin Engineering Co, Ltd. |  |  |  |  | Level 3: 0.000655; Level 5: 0.000654
|  | Senboku Natural Gas Power Generation Co., Ltd. |  |  |  |  | Level 3: 0.000388; Level 5: 0.000385
|  | Diamond Power Corp. |  |  |  |  | Level 3: 0.000431; Level 5: 0.000427
|  | Tess Engineering Co.,Ltd. |  |  |  |  | Level 3: 0.000494; Level 5: 0.00049
|  | Tokyo Eco Service Co., Ltd. |  |  |  |  | Level 3: 9.2e-05; Level 5: 9.1e-05
|  | Nihon Techno Co., Ltd. |  |  |  |  | Level 3: 0.000508; Level 5: 0.000509
|  | Japan Logistic Coop. |  |  |  |  | Level 3: 0.000486; Level 5: 0.000256
|  | Panasonic Corp. |  |  |  |  | Level 3: 0.000498; Level 5: 0.000492
|  | Premium Green Power Corp. |  |  |  |  | Level 3: 1.8e-05; Level 5: 2.2e-05
|  | Marubeni Corp. |  |  |  |  | Level 3: 0.000378; Level 5: 0.000324
|  | Mitsuuroko Green Energy Co., Ltd. |  |  |  |  | Level 3: 0.000366; Level 5: 0.000445
|  | Les Power Co.,Ltd. |  |  |  |  | Level 3: 0.00042; Level 5: 0
|  | Alternative value |  |  |  |  | Level 3: 0.00055
CO2 emission intensity by building type
|  | Building Type |  |  |  | 評価建物 | Level 3: Primary energy consumption by building size [MJ/m2-yr]; Level 5: Primary energy composition per energy source | CO2 emission
[7 empty] | 300 | 2000 | 10000 | 30000 |  | #VALUE! | 0.0498 | 0.06855
[7 empty] | less than 300m2 | over 300m2 and less that 2,000m2 | over 2,000m2 and less that 10,000m2 | over 10,000m2 and less that 30,000m2 | over 30,000m2 | Electricity | Town gas | Other * | LPG | intensity kg-CO2/MJ
|  | Office | Office |  | 0 | 0 | 1540 | 1540 | 1540 | 1930 | 2270 | 90% | 6% | 4% | - | #VALUE!
|  |  | Government buildings |  | 0 | 0 | 1100 | 1100 | 1100 | 1260 | 1380 | 83% | 9% | 8% | - | #VALUE!
|  | School | Kindergartens/ nursery schools |  | 0 | 0 | 490 | 490 | 490 | 490 | 490 | 71% | 16% | 13% | - | #VALUE!
|  |  | ES/JHS | Hokkaido | 0 | 0 | 522 | 522 | 522 | 522 | 522 | 62.3% | 16.72% | 20.98% | - | #VALUE!
|  |  |  | Other area | 0 | 0 | 310 | 310 | 310 | 310 | 310 | 76% | 13.55% | 10.45% |  | #VALUE!
|  |  | High schools |  | 0 | 0 | 390 | 390 | 390 | 360 | 240 | 74% | 7% | 19% | - | #VALUE!
|  |  | Universities/ colleges |  | 0 | 0 | 880 | 880 | 880 | 850 | 1160 | 79% | 12% | 9% | - | #VALUE!
|  | Retailers | Department, supermarkets |  | 0 | 0 | 7430 | 7430 | 5130 | 3190 | 3190 | 93% | 3% | 4% | - | #VALUE!
|  |  | Other stores |  | 0 | 0 | 2360 | 2360 | 2360 | 2950 | 2680 | 92% | 4% | 4% | - | #VALUE!
|  | Restaurants |  |  | 0 | 0 | 2960 | 2960 | 2960 | 2960 | 2960 | 50% | 38% | 12% | - | #VALUE!
|  | Halls | Theatres/halls |  | 0 | 0 | 1030 | 1030 | 1030 | 1450 | 1670 | 76% | 16% | 8% | - | #VALUE!
|  |  | Exhibition facilities |  | 0 | 0 | 1120 | 1120 | 1120 | 1580 | 1220 | 81% | 9% | 10% | - | #VALUE!
|  |  | Sports facilities |  | 0 | 0 | 1910 | 1910 | 1910 | 1300 | 1130 | 92% | 6% | 2% | - | #VALUE!
|  | Factories |  |  | 0 | 0 | 498 | 498 | 498 | 498 | 498 | 100% | 0% | 0% | - | #VALUE!
|  | Hospitals |  |  | 0 | 0 | 2210 | 2210 | 2210 | 2450 | 2920 | 65% | 15% | 20% | - | #VALUE!
|  | Hotels |  |  | 0 | 0 | 2440 | 2440 | 2440 | 2740 | 2740 | 77% | 10% | 13% | - | #VALUE!
[5 empty] | 0 | 0 | Level 5: #VALUE!; Level 3: 0.0498; Level 4: 0.0678; Level 5: 0.059
|  | Apartments | Private area |  |  | - | - | - | - | - | - | 51% | 21% | 18% | 10% | #VALUE!
|  |  | Common area |  |  | - | - | - | - | - | - | 100% | 0% | 0% | - | #VALUE!
|  | 評価建物 | [13 empty] | #VALUE! | bar: Level 3 to Level 4; Level 5
|  | Source; | Summary of DECC data-base for Energy Consumption of Commercial Building (released in April 2013, JSBC) |  |  |  | Level 4: * Kerosene for Apt.
The primary energy composition ratio of private areas of apartments is in reference to "Final energy consumption by energy type in residential sector (Energy demand and supply record in 2011, the Agency of Natural Resources and Energy)." Regarding factories, since there is no statistical data available, the energy consumption for lighting in office buildings under the Notification No. 7 of 2013 Energy Conservation Law is used.
As for restaurants, data from buildings having a total floor space of more than 2,000 m2 are compiled.
LR1/3c Primary energy consumption used for calculating CO2 emissions by using specification energy standard (MJ/m2)
|  | Type of HVAC |  | Assessment level in LR1.3c. |  |  | Level 3: Subject Bldg.; Level 4: Climate zone; Level 4: MJ/㎡-yr |  | 「－」の場合
|  | Heating | Cooling |  |  | 1 | #N/A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  |  |  | Ref. Bldg. | Aa0 | 2 | #N/A | 1484 | 1298 | 1189 | 1246 | 1163 | 1100 | 976 | 888 |  | 1721 | 1502 | 1413 | 1464 | 1374 | 1343 | 1164 | 1017
|  | A | a | Level 1 | Aa1 | 3 | #N/A | 1721 | 1502 | 1373 | 1440 | 1343 | 1268 | 1121 | 1017 |  | 1484 | 1298 | 1223 | 1266 | 1190 | 1163 | 1012 | 888
|  |  |  | Level 4 | Aa4 | 4 | #N/A | 1365 | 1196 | 1097 | 1149 | 1074 | 1016 | 903 | 823
|  |  |  | Ref. Bldg. | Ab0 | 5 | #N/A | 1466 | 1282 | 1155 | 1179 | 1092 | 926 | 752 | 556
|  | A | b | Level 1 | Ab1 | 6 | #N/A | 1700 | 1483 | 1333 | 1361 | 1258 | 1063 | 857 | 625
|  |  |  | Level 4 | Ab4 | 7 | #N/A | 1348 | 1182 | 1066 | 1088 | 1009 | 858 | 700 | 521
|  |  |  | Ref. Bldg. | Ba0 | 8 | #N/A | 1374 | 1287 | 1223 | 1266 | 1190 | 1163 | 1012 | 888
|  | B | a | Level 1 | Ba1 | 9 | #N/A | 1592 | 1489 | 1413 | 1464 | 1374 | 1343 | 1164 | 1017
|  |  |  | Level 4 | Ba4 | 10 | #N/A | 1265 | 1186 | 1128 | 1167 | 1098 | 1074 | 936 | 823
|  |  |  | Ref. Bldg. | Bｂ0 | 11 | #N/A | 1356 | 1271 | 1189 | 1199 | 1119 | 990 | 789 | 556
|  | B | b | Level 1 | Bｂ1 | 12 | #N/A | 1571 | 1470 | 1373 | 1385 | 1290 | 1137 | 900 | 625
|  |  |  | Level 4 | Bｂ4 | 13 | #N/A | 1249 | 1172 | 1097 | 1106 | 1033 | 916 | 733 | 521
|  |  |  | Ref. Bldg. | Ca0 | 14 | #N/A | 1024 | 966 | 916 | 941 | 856 | 901 | 869 | 888
|  | C | a | Level 1 | Ca1 | 15 | #N/A | 1178 | 1110 | 1050 | 1080 | 97 | 1033 | 995 | 1017
|  |  |  | Level 4 | Ca4 | 16 | #N/A | 947 | 894 | 849 | 871 | 794 | 835 | 806 | 823
|  |  |  | Ref. Bldg. | Cｂ0 | 17 | #N/A | 1006 | 950 | 882 | 874 | 784 | 727 | 646 | 556
|  | C | b | Level 1 | Cｂ1 | 18 | #N/A | 1157 | 1091 | 1010 | 1001 | 895 | 828 | 731 | 625
|  |  |  | Level 4 | Cｂ4 | 19 | #N/A | 931 | 880 | 818 | 811 | 729 | 677 | 603 | 521
|  | － | － | Assessed by primary energy calculation | －－Assessed by primary energy calculation | - | #N/A
[5 empty] | －－0 | - | #N/A
*Reference value = Level 3
d. LCCO2 Calculation Conditions
| Service life of building structure (years） | [5 empty] | S | Climate zone 3: RC; Climate zone 6: SRC
|  | Q2/2.2.1 Service Life of Structural Frame Materials |  |  |  |  | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5
|  |  | Office |  | 1 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | School |  | 2 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Retailers |  | 3 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Restaurants |  | 4 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Halls |  | 5 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Factories |  | 6 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Hospitals |  | 7 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Hotels |  | 8 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Apartments |  | 9 |  | 30 | 60 | 90 | 30 | 60 | 90 | 30 | 60 | 90
| Representative Quantities of Materials | [5 empty] | No Reuse | Existing Structure 100% | Blast furnace cement100% | No Reuse | Existing Structure 100% | Blast furnace cement100% | No Reuse | Existing Structure 100% | Blast furnace cement100%
|  | Office | Regular concrete | m3/m2 |  |  | 0.567 | 0 | 0 | 0.772 | 0 | 0 | 0.696 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.567 | 0 | 0 | 0.772 | 0 | 0 | 0.696
|  |  | Steel frame | t/m2 |  |  | 0.136 | 0 | 0.136 | 0.038 | 0 | 0.038 | 0.1 | 0 | 0.1
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.07 | 0 | 0.07 | 0.103 | 0 | 0.103 | 0.078 | 0 | 0.078
|  |  | Timber | t/m2 |  |  | 0.005 | 0 | 0.005 | 0.013 | 0 | 0.0126 | 0.008 | 0 | 0.008
|  | School | Regular concrete | m3/m2 |  |  | 0.352 | 0 | 0 | 0.865 | 0 | 0 | 0.958 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.352 | 0 | 0 | 0.865 | 0 | 0 | 0.958
|  |  | Steel frame | t/m2 |  |  | 0.105 | 0 | 0.105 | 0.005 | 0 | 0.005 | 0.078 | 0 | 0.078
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.045 | 0 | 0.045 | 0.112 | 0 | 0.112 | 0.11 | 0 | 0.11
|  |  | Timber | t/m2 |  |  | 0.002 | 0 | 0.0024 | 0.015 | 0 | 0.0147 | 0.012 | 0 | 0.01167
|  | Retailers | Regular concrete | m3/m2 |  |  | 0.342 | 0 | 0 | 0.888 | 0 | 0 | 0.307 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.342 | 0 | 0 | 0.888 | 0 | 0 | 0.307
|  |  | Steel frame | t/m2 |  |  | 0.072 | 0 | 0.072 | 0.017 | 0 | 0.017 | 0.071 | 0 | 0.071
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.024 | 0 | 0.024 | 0.118 | 0 | 0.118 | 0.053 | 0 | 0.053
|  |  | Timber | t/m2 |  |  | 0.002 | 0 | 0.00186 | 0.015 | 0 | 0.0148 | 0.005 | 0 | 0.00483
|  | Restaurants | Regular concrete | m3/m2 |  |  | 0.342 | 0 | 0 | 0.888 | 0 | 0 | 0.307 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.342 | 0 | 0 | 0.888 | 0 | 0 | 0.307
|  |  | Steel frame | t/m2 |  |  | 0.072 | 0 | 0.072 | 0.017 | 0 | 0.017 | 0.071 | 0 | 0.071
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.024 | 0 | 0.024 | 0.118 | 0 | 0.118 | 0.053 | 0 | 0.053
|  |  | Timber | t/m2 |  |  | 0.002 | 0 | 0.00186 | 0.015 | 0 | 0.0148 | 0.005 | 0 | 0.00483
|  | Halls | Regular concrete | m3/m2 |  |  | 0.345 | 0 | 0 | 0.888 | 0 | 0 | 0.862 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.345 | 0 | 0 | 0.888 | 0 | 0 | 0.862
|  |  | Steel frame | t/m2 |  |  | 0.139 | 0 | 0.139 | 0.017 | 0 | 0.017 | 0.059 | 0 | 0.059
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.04 | 0 | 0.04 | 0.118 | 0 | 0.118 | 0.1 | 0 | 0.1
|  |  | Timber | t/m2 |  |  | 0.004 | 0 | 0.00435 | 0.015 | 0 | 0.0148 | 0.012 | 0 | 0.01227
|  | Factories | Regular concrete | m3/m2 |  |  | 0.354 | 0 | 0 | 0.77 | 0 | 0 | 0.669 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.354 | 0 | 0 | 0.77 | 0 | 0 | 0.669
|  |  | Steel frame | t/m2 |  |  | 0.088 | 0 | 0.088 | 0.01 | 0 | 0.01 | 0.077 | 0 | 0.077
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.031 | 0 | 0.031 | 0.108 | 0 | 0.108 | 0.08 | 0 | 0.08
|  |  | Timber | t/m2 |  |  | 0.002 | 0 | 0.0021 | 0.009 | 0 | 0.00915 | 0.007 | 0 | 0.00669
|  | Hospitals | Regular concrete | m3/m2 |  |  | 0.317 | 0 | 0 | 0.766 | 0 | 0 | 0.812 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.317 | 0 | 0 | 0.766 | 0 | 0 | 0.812
|  |  | Steel frame | t/m2 |  |  | 0.074 | 0 | 0.074 | 0.012 | 0 | 0.012 | 0.66 | 0 | 0.066
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.034 | 0 | 0.034 | 0.096 | 0 | 0.096 | 0.089 | 0 | 0.089
|  |  | Timber | t/m2 |  |  | 0.002 | 0 | 0.002 | 0.013 | 0 | 0.013 | 0.01 | 0 | 0.00969
|  | Hotels | Regular concrete | m3/m2 |  |  | 0.436 | 0 | 0 | 0.999 | 0 | 0 | 0.816 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.436 | 0 | 0 | 0.999 | 0 | 0 | 0.816
|  |  | Steel frame | t/m2 |  |  | 0.103 | 0 | 0.103 | 0.004 | 0 | 0.004 | 0.084 | 0 | 0.084
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.034 | 0 | 0.034 | 0.111 | 0 | 0.111 | 0.093 | 0 | 0.093
|  |  | Timber | t/m2 |  |  | 0.005 | 0 | 0.00471 | 0.014 | 0 | 0.01434 | 0.012 | 0 | 0.01248
|  | Apartments | Regular concrete | m3/m2 |  |  | 0.323 | 0 | 0 | 0.734 | 0 | 0 | 0.75 | 0 | 0
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.323 | 0 | 0 | 0.734 | 0 | 0 | 0.75
|  |  | Steel frame | t/m2 |  |  | 0.048 | 0 | 0.048 | 0.012 | 0 | 0.012 | 0.052 | 0 | 0.052
|  |  | Steel frame (Electric furnace） | t/m2 |  |  |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  |  | Steel reinforcement | t/m2 |  |  | 0.019 | 0 | 0.019 | 0.1 | 0 | 0.1 | 0.136 | 0 | 0.136
|  |  | Timber | t/m2 |  |  | 0.002 | 0 | 0.00198 | 0.013 | 0 | 0.01329 | 0.125 | 0 | 0.1251
Renewal interval (years)
|  | Exterior |  |  |  |  | S Level 3: 25; S Level 4: years
Roof
|  | Interior |  |  |  |  | S Level 3: 18; S Level 4: years
|  | Building Service |  |  |  |  | S Level 3: 15; S Level 4: years
Repair rate
|  | Exterior |  |  |  |  | S Level 3: 1%; S Level 4: /yr
|  | Interior |  |  |  |  | S Level 3: 1%; S Level 4: /yr
|  | Building Service |  |  |  |  | S Level 3: 2%; S Level 4: /yr

## Credit
Comprehensive Assessment System for Built Environment Efficiency
CASBEE for Building (New Construction)
Microsoft Excel 2013
CASBEE-BD_NCe_2014 v.2.1
Published in February 2015
Software development: Japan Sustainable Building Consortium (JSBC)
(Research Committee, Comprehensive Assessment System for Built Environment Efficiency)
Planning and publication: Institute for Building Environment and Energy Conservation (IBEC)
Inquiries concerning software content, etc. :
Inquiries concerning the content of this software should be sent by e-mail only to the address below. A few days may be required before you receive a reply. Please refer to the manuals for Microsoft Windows, Microsoft Excel 2013, and other software for instructions on their use.
Institute for Building Environment and Energy Conservation
2F Zenkyouren Building Kojimachi-kan, 3-5-1 Kojimachi, Chiyoda-ku, Tokyo 102-0083 Japan
E-mail: casbee-info@ibec.or.jp
URL: http://www.ibec.or.jp/
Copyright ©2015 Institute for Building Environment and Energy Conservation (IBEC)
Important Notes(Conditions of Use)
1) Microsoft Excel 2013 is a registered trademark of Microsoft Corporation in the United States of America and other countries.
2) Other company names and product names are trademarks or registered trademarks of the companies concerned.
3) CASBEE for Building (New Construction) consists of data files that were developed using Microsoft Excel 2013. These data files are protected by copyright law. They may not be duplicated or transferred (even in modified form) without the consent of the developers, authors, planners, and publishers.
4) This restriction does not apply to the use of input data and output results prepared on this software by its users. In such cases, the data concerned should include a statement to the effect that it was prepared using this assessment software. Note that the additional consent of Microsoft Corporation may be required for the use of screen images.
5) We accept no liability for the results of using this software or its instruction manual.
6) The specifications of this software and the contents of the operation manual are subject to change without prior notice.
7) This software was created using Microsoft Excel 2013. We do not guarantee its operation on all computers.